## Slide 1: Modern Hydro Power Plants
Prof. Dr.sc. Gordana Janevska

## Slide 2: Hydro Power Plants: Basics, types and classification, principle of operation
Energy utilization
Electricity generation and consumption
Types of power plants
Types of Hydropower Plants
  Types of hydroelectric power plants according to the method of water utilization
  Types of hydroelectric power plants based on the available head
  Types of hydroelectric power plants according to installed capacity
  Hybrid hydropower
Environmental and Social Aspects of Hydro Power Plants
  Fish migration
  Sedimentation
  Water quality
  Environmental flows
  Hydropeaking
  Mitigation hierarchy
Principle of Operation of Hydroelectric Power Plants
  Available and useful energy head of the turbine
  Turbine Power and Efficiency

## Slide 3: 1.4. Types of Hydropower Plants
Different classifications of hydropower plants are used, depending on the parameters that are considered dominant in the specific analyses, such as:
The way of water utilization,
The location of the plants themselves,
The height of the available head,
The size of the reservoir,
Capacity - installed power,
Type of turbines,
Distance of the machine building (powerhouse) from the dam,
Location of the powerhouse,
Role in the power system, etc.
Hydro Power Plants:
Basics, types and classification, principle of operation

## Slide 4: 1.4. Types of Hydropower Plants
According to the location of the plants themselves, hydropower plants can be:
Conventional hydropower plants (on watercourses: rivers, streams, canals, etc.)
Tidal hydropower plants - utilizing the potential difference in the levels of tides (high and low tides)
Sea wave hydropower plants - harnessing the kinetic energy of waves.
According to the size of the reservoir, hydropower plants can be:
Daily storage hydropower plants (the reservoir is filled during the night and emptied during the day)
Seasonal storage hydropower plants (the reservoir is filled during the rainy season and emptied during the dry season),
Year-round storage hydropower plants (the reservoir is filled during rainy years and emptied during dry years).
According to the distance between the powerhouse and the dam, hydropower plants can be:
Run-of-river plants (the powerhouse is located near the dam, inside the dam, or is a part of the dam),
Derivational plants (the powerhouse is located far away from the dam).
Hydro Power Plants:
Basics, types and classification, principle of operation

## Slide 5: 1.4. Types of Hydropower Plants
According to the location of the powerhouse, hydropower facilities can be:
Surface hydropower plants with powerhouse located in open space,
Underground hydropower plants with a buried powerhouse.
According to the role in the power system, hydroelectric facilities can be:
Base hydropower plants, whose operational characteristics allow them to fulfill the base (permanent) part of the load diagram,
Peak hydropower plants, whose operational characteristics are adapted to fulfill the peak (variable) part of the load diagram.
Hydro Power Plants:
Basics, types and classification, principle of operation

## Slide 6: 1.4. Types of Hydropower Plants 1.4.1. Types of hydroelectric power plants according to the method of water utilization
According to the method of water utilization, hydroelectric power plants can be classified as:
Storage hydroelectric power plants, which have a reservoir where water is accumulated during rainy periods (or periods of low demand) and used according to the needs;
Run-of-river hydroelectric power plants, which utilize water based on its natural flow;
Reversible hydroelectric power plants, also known as pumped-storage hydroelectric power plants, which have two reservoirs (upper and lower). During times of excess electrical energy (or periods of low demand), water is pumped from the lower to the upper reservoir to be used for generating electricity during peak consumption (high demand) periods.
Hydro Power Plants:
Basics, types and classification, principle of operation

## Slide 7: 1.4. Types of Hydropower Plants 1.4.1. Types of hydroelectric power plants according to the method of water utilization
Storage (Accumulation) hydroelectric power plants are built on watercourses, where with economically feasible costs, by blocking the river and creating a dam, an accumulation lake can be formed downstream of the dam. The water in the reservoir represents an energy reservoir and possesses potential energy resulting from the difference in elevation between the upper level of the lake and the point of installation of the generator. This energy is converted into kinetic energy of the water, which, under the influence of turbine blades, is transformed into pressure energy. Acting on the turbine blades, it produces the mechanical energy that drives the turbines. These types of power plants usually experience significant annual variations in the amount of water flow and the water level in the accumulation lake.
Hydro Power Plants:
Basics, types and classification, principle of operation
Scheme of a storage hydropower plant

## Slide 8: 1.4. Types of Hydropower Plants 1.4.1. Types of hydroelectric power plants according to the method of water utilization
Run-of-river hydroelectric power plants are power plants where, due to any reason, it is not possible to create an accumulation basin, and all the water that normally flows into the watercourse is used at the moment of inflow, flowing through the turbine, or it overflows unused through the dam. They have a small difference in elevation between the water intake and the outflow, meaning they do not utilize the potential energy from the level difference, but only the kinetic energy possessed by the water flow. The capacity of these power plants depends on the instantaneous water flow, as they can generate electricity only in accordance with the natural water inflow regime, that is, in accordance with the natural conditions and flows.
Hydro Power Plants:
Basics, types and classification, principle of operation
Run-of-river hydropower plant (Chief Joseph Dam, US)

## Slide 9: 1.4. Types of Hydropower Plants 1.4.1. Types of hydroelectric power plants according to the method of water utilization
Reversible hydroelectric power plants (pumped-storage hydropower plants) are structurally similar to storage hydropower plants. These power plants have two accumulation basins - upper and lower. In turbine mode, water from the upper reservoir is directed into the turbine impeller (turbine mode of operation), and the facility operates as a storage hydroelectric plant, generating electrical energy. In the pumping mode of operation, using reversible turbines, water from the lower basin is pumped back into the upper basin, and the facility operates as a consumer. They are energy/balance inefficient since the energy consumption of the pump in pumping mode is greater than the production in turbine mode. However, their advantage is that water can be pumped back into the upper basin during periods of low demand (cheaper tariffs) and then used to generate electrical energy during peak periods (higher tariffs). Their primary use is to cover peak loads and improve the utilization of available power plants. Pumped-storage hydropower plants fill the depression in the daily load diagram and take over the coverage of peak loads. This means that for the remaining power plants in an energy system, the load diagram becomes significantly more uniform and favorable.
Hydro Power Plants:
Basics, types and classification, principle of operation
Pumped storage hydropower plant

## Slide 10: 1.4. Types of Hydropower Plants 1.4.2. Types of hydroelectric power plants based on the available head
According to the available head, hydroelectric power plants can be classified as:
Low-head, with a head 𝐻 < 40 m;
Medium-head, with a moderate head 𝐻 = 40 - 100 m;
High-head, with large heads 𝐻 > 100 m.
Hydro Power Plants:
Basics, types and classification, principle of operation

## Slide 11: 1.4. Types of Hydropower Plants 1.4.2. Types of hydroelectric power plants based on the available head
Low-head hydroelectric power plants
There are two types of low-head hydroelectric power plants: river-based and canal-based.
The external characteristic of a river-based low-head hydroelectric power plant consists of the dam, the water intake structure leading to the turbine, and the turbine unit with the generator, forming a complete system.
For low-head river hydroelectric power plants, primarily Kaplan and Francis turbines are installed due to the small heads and large water flows. For heads up to 20 m, pipe turbines in a so-called bulb configuration are also used. An example of a low-head river power plant is the Gjerdap hydroelectric power plant.
Hydro Power Plants:
Basics, types and classification, principle of operation
Low-head river hydroelectric power plants

## Slide 12: 1.4. Types of Hydropower Plants 1.4.2. Types of hydroelectric power plants based on the available head
Low-head hydroelectric power plants
Low-head canal hydroelectric power plants differ from river-based ones in that, in addition to the head obtained by constructing a dam, they also utilize the natural slope of the river channel over a certain distance. For this purpose, an additional canal with a slight slope needs to be constructed, and at its end, the powerhouse is located.
Hydro Power Plants:
Basics, types and classification, principle of operation
Low-head channel hydroelectric power plant (Varazdin)
A - Turbine field, B - Flow control field, C – 110 kV switchyard, D - Access road, E - Concrete membrane, F - Parking lot

## Slide 13: 1.4. Types of Hydropower Plants 1.4.2. Types of hydroelectric power plants based on the available head
Medium-head hydroelectric power plants
In medium-head hydroelectric power plants, the necessary head is obtained by constructing embankments or concrete (gravity or arch) dams, behind which the powerhouse and electrical distribution equipment are incorporated. Depending on the terrain characteristics, all the structures can be designed as a single construction unit or individual components can be located separately.
Medium-head power plants can be implemented as run-of-river or diversion power plants. They are constructed at locations where the river bends, and then canals or pipelines are built. Francis turbines are used for medium heads, where the guiding apparatus with blades surrounds the runner. In these turbines, the potential energy of the water is only partially converted into kinetic energy in the guiding apparatus, so that with a certain excess pressure, it reaches the runner and transfers its energy to it.
Hydro Power Plants:
Basics, types and classification, principle of operation
Medium-head hydroelectric power plant with concrete gravity dam (Potpech)

## Slide 14: 1.4. Types of Hydropower Plants 1.4.2. Types of hydroelectric power plants based on the available head
High-head hydroelectric power plants
Depending on whether they have or do not have an accumulation basin (reservoir), high-head hydroelectric power plants can be categorized as: high-head power plants without accumulation and high-head power plants with accumulation.
Hydro Power Plants:
Basics, types and classification, principle of operation
High-head derivation hydropower plant (Dubrovnik)
Underground powerhouse of high-head hydroelectric power plant (HPP Split)
1 - Intake structure, 2 - Inlet tunnel, 3 - Pressure conduit, 4 - Water chamber, 5 - Gate chamber, 6 - Pressure pipeline. 7 – Powerhouse, 8 - Tailrace channel
1 - Inlet tunnel, 2 - Water chamber I, 3 - Water chamber II, 4 - Gate chamber, 5 - Pressure conduit, 6 – Powerhouse, 7 – Substation, 8 - Pressure tunnel, 9 - Inlet tunnel, 10 - Cable tunnel

## Slide 15: 1.4. Types of Hydropower Plants 1.4.3. Types of hydroelectric power plants according to installed capacity
According to the installed capacity, hydroelectric power plants are categorized as:
Large hydroelectric power plants (usually 10 MW or more),
Small hydroelectric power plants (according to the criteria of most European countries, up to 10 MW),
Micro hydroelectric power plants (primarily up to 100 kW), and
Pico hydroelectric power plants (primarily below 5 kW).
Hydro Power Plants:
Basics, types and classification, principle of operation

## Slide 16: 1.4. Types of Hydropower Plants 1.4.3. Types of hydroelectric power plants according to installed capacity
Small hydropower plants
It is believed that small hydropower plants have no negative impact on the environment, and this is where their advantage lies. The term "small hydroelectric power plant" is not precisely defined and varies from country to country. Such power plants are often classified as mini and micro hydroelectric power plants. They are suitable for low-energy decentralized areas (island-based). In addition to being owned by large energy companies, they can also be owned by smaller private companies.
Compared to large hydropower plants, some of the benefits of small hydropower plants are as follows:
Short construction period, significantly impacting the quality of life in the environment;
Long operational lifespan and investment security;
No negative impact on the ecosystem as seen with large hydroelectric power plants;
Cost-effective maintenance.
Hydro Power Plants:
Basics, types and classification, principle of operation

## Slide 17: 1.4. Types of Hydropower Plants 1.4.3. Types of hydroelectric power plants according to installed capacity
Large hydropower plants
Large hydropower plants are massive constructions, and their typical capacity ranges from several hundred MW to over 20 GW.
The impact of large hydropower plants on the ecosystem depends on four factors:
The velocity and volume of water within the river where the power plant is located;
The shape of the environment, surrounding conditions, and climatic factors prior to the plant's construction;
The construction of the power plant, its size, and operational methods;
If multiple power plants are built on the same river, the impact of one plant on the ecosystem may depend on the other plants.
Hydro Power Plants:
Basics, types and classification, principle of operation

## Slide 18: 1.4. Types of Hydropower Plants
According to the type of installed turbines, hydroelectric power plants are divided into:
Impulse turbines, which include impulse water turbines (such as Pelton turbines) that utilize only the kinetic energy of the water flow, where the entire available head is converted into inlet velocity;
Reaction turbines, which include reaction water turbines (such as Francis, Kaplan, propeller, tube turbines, etc.) that utilize both the available pressure and kinetic energy of the river flow, where the entire available head is not used to create the inlet velocity of the water into the turbine.
Hydro Power Plants:
Basics, types and classification, principle of operation

## Slide 19: 1.4. Types of Hydropower Plants 1.4.4. Hybrid hydropower
In addition to the previously mentioned types of hydropower plants, it is worth highlighting the concept of hybrid power plants. Hybrid power plants function as an integrated unit with one or more distinct forms of power generation and can either be situated on a single site or constitute a microgrid. Hybrid power plants may be connected to the grid or be located far from the grid in remote regions, where they serve as the primary energy source. Within hybrid power plants, hydroelectric power can be paired with either solar or wind energy to enhance the stability and reliability of electricity generation. This hybridization enables photovoltaic (PV) panels or wind turbines to generate electricity when sunlight or wind is available, while saving water for hydroelectric power generation during periods when sunlight or wind conditions are intermittent.
Hydro Power Plants:
Basics, types and classification, principle of operation
Hybrid power plant combining seawater pumped storage, wind and/or solar power generation with a desalination plant (Source: Voith)

## Slide 20: 1.4. Types of Hydropower Plants 1.4.4. Hybrid hydropower
Hybrid solar – hydro power system
A hybrid plant utilizing hydro and solar energy for the generation of electrical energy, applied to overcome the impact of climate change on the hydropower plant. When the river flow is less than the desired rate, solar energy is then used to manage the load.
Hydro Power Plants:
Basics, types and classification, principle of operation
Hybrid floating PV-hydropower system

## Slide 21: 1.4. Types of Hydropower Plants 1.4.4. Hybrid hydropower
Hybrid wind - hydro power plant
In these facilities, energy is stored as potential energy in the water reservoir, compensating for reduced hydroelectric production during periods when there is sufficient energy production from the wind power plant.
Hydro Power Plants:
Basics, types and classification, principle of operation
Hybrid wind – hydro power plant

## Slide 22: 1.4. Types of Hydropower Plants 1.4.4. Hybrid hydropower
Hybrid solar – wind – hydro power plant
The hybrid solar – wind – hydro power system could produce and store electrical energy at lower costs and achieve a reduction in CO2 emissions. When designing such a system, it is essential to pay attention to the proper combination of all factors for the solution to be optimal. By integrating and combining various renewable energy sources into one system, it contributes to reducing electricity costs, increasing energy supply security from renewable sources, and working towards the goal of reliability in hybrid energy solutions.
Hydro Power Plants:
Basics, types and classification, principle of operation
Hybrid RES system, wind – solar – hydro power plant

## Slide 23: 1.4. Types of Hydropower Plants 1.4.4. Hybrid hydropower
Modern hybrid hydro power plants represent innovative and integrated systems that combine various energy sources to enhance the efficiency and sustainability of electricity generation.
The advantages and various possibilities for combining different energy sources make modern hybrid hydro power plants significant in the pursuit of a sustainable and innovative energy sector. They serve a crucial role in the energy transition as innovative and sustainable solutions for electricity generation.
Hydro Power Plants:
Basics, types and classification, principle of operation