## Slide 1: Modern Hydro Power Plants
Prof. Dr.sc. Gordana Janevska

## Slide 2: Hydro Power Plants: Basics, types and classification, principle of operation
Energy utilization
Electricity generation and consumption
Types of power plants
Types of Hydropower Plants
  Types of hydroelectric power plants according to the method of water utilization
  Types of hydroelectric power plants based on the available head
  Types of hydroelectric power plants according to installed capacity
  Hybrid hydropower
Environmental and Social Aspects of Hydro Power Plants
  Fish migration
  Sedimentation
  Water quality
  Environmental flows
  Hydropeaking
  Mitigation hierarchy
Principle of Operation of Hydroelectric Power Plants
  Available and useful energy head of the turbine
  Turbine Power and Efficiency

## Slide 3: 1.6. Principle of Operation of Hydroelectric Power Plants
Hydro Power Plants:
Basics, types and classification, principle of operation
Hydro energy, derived from water as a working fluid, is recognized as a form of renewable energy since it essentially involves the conversion of solar radiation into usable energy. It is characterized by cyclic regeneration within specific time periods.
s – cross-sectional area of the pipe/profile,
E - energy contained in a certain quantity of water in the cross-section,
P - power of the water flow,
Q - water flow rate,
p – overpressure relative to atmospheric,
v=Q/s – mean velocity of water flow through the pipe cross-section,
h – height of the center of gravity of the cross-section relative to the reference plane,
Flow of water through the considered pipe

## Slide 4: 1.6. Principle of Operation of Hydroelectric Power Plants
Hydro Power Plants:
Basics, types and classification, principle of operation
To conduct energy analyses on water, it is crucial to understand two fundamental equations that describe its properties and states: The Bernoulli equation and the equation of continuity.
The Bernoulli equation given by expression demonstrates that the head/pressure drop of waterН in (m) is equal to the sum of three heights: static height, geometric height, and piezometric velocity, i.e.:
H=e/g=(αv2)/2g+h+p/ρg
e – water flow energy, which is a sum of three energies: unit kinetic energy, unit potential energy and unit pressure energy,
g - acceleration due to gravity
α - Coriolis coefficient (α<1)
v – mean velocity of water flow
ρ – density of water.
Continuity equation, According to this equation, the same quantity of fluid Q passes through each of its cross-sections Ѕ (Ѕ1, Ѕ2, Ѕ3,...) per second. In other words, for a segment of the pipeline with no source or sink, the flow rate of the fluid remains constant in every cross-section :
Q=v1 S1=v2 S2=v3 S3=const

## Slide 5: 1.6. Principle of Operation of Hydroelectric Power Plants
Hydro Power Plants:
Basics, types and classification, principle of operation
Hydroelectric power plants are facilities where the potential and kinetic energy of water is converted into mechanical energy through water turbines and further transformed into electrical energy by means of electric generators. The operational capability of the water flow depends on the water quantity (flow rate) and the difference in elevation between the lower and upper water surfaces, known as the head. If the difference between the lower and upper levels is [m], the water flow rate is [m3/s], its density is [kg/m3] and the acceleration due to gravity is [m/s2] the available theoretical power [W] will be as follows:

## Slide 6: 1.6. Principle of Operation of Hydroelectric Power Plants 1.6.1. Available and useful energy head of the turbine
Hydro Power Plants:
Basics, types and classification, principle of operation
The difference in elevation between the free water surfaces in the reservoir 1 and the tailrace canal 7 represents the available or gross energy head, i.e., the hydraulic head, which is commonly referred to as the gross head or simply the head. However, the entire gross head cannot be fully utilized due to losses that occur in the pipeline. Therefore, the useful or net energy head, also known as the net head, is defined.
Hydropower plant
е – net energy head,
еI – specific energy of water in the reservoir,
еII – specific energy of water at the turbine outlet,
ezag – hydraulic losses in the pipeline.
the siphon is designed as a diffuser, which reduces the velocity

## Slide 7: 1.6. Principle of Operation of Hydroelectric Power Plants 1.6.1. Available and useful energy head of the turbine
Hydro Power Plants:
Basics, types and classification, principle of operation
Hydropower plant
In an existing hydroelectric power plant, the specific energy can be experimentally determined by measuring the flow rate and the static pressures in the inlet pipe just before the turbine and in the outlet pipe. For this purpose, a pressure gauge is used, which indicates the gauge pressure relative to the external atmospheric pressure
is the distance to the pressure gauge

## Slide 8: 1.6. Principle of Operation of Hydroelectric Power Plants 1.6.2. Turbine Power and Efficiency
Hydro Power Plants:
Basics, types and classification, principle of operation
Water turbines (hydroturbines) are characterized not only by the specific energy (net head) [J/kg], which is exchanged per kilogram of water, but also by the mass flow rate [kg/s] of water through the turbine. Assuming that the energy exchange is ideal, without losses, the ideal (theoretical) power would be:
The efficiency factor represents the ratio of the utilized energy or power to the available energy , or respective ideal power .
If the total hydraulic losses in the turbine are , the water will be able to transfer energy to the turbine runner, where is referred to as the hydraulic or theoretical specific energy of the turbine.
Hydraulic efficiency

## Slide 9: 1.6. Principle of Operation of Hydroelectric Power Plants 1.6.2. Turbine Power and Efficiency
Hydro Power Plants:
Basics, types and classification, principle of operation
If the total flow rate is , the volumetric losses are , then the flow rate through the turbine impeller is .
Volumetric efficiency
The internal power , or the power transferred to the turbine wheel:
Effective (external) power , which represents the power obtained at the turbine shaft and can be delivered to the generator.
Mechanical efficiency
The total efficiency of the turbine or, briefly, the overall efficiency