## Slide 1: Modern Hydro Power Plants
Prof. Dr.sc. Gordana Janevska

## Slide 2: Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
Description and classification
  Pelton turbine
  Francis Turbine
  Propeller and Kaplan turbines
  Horizontal axis turbine
  Diagonal turbine
Flow through the runner in reaction turbines
Basic energy equation for turbines (Euler's equation)
Similarity in hydroturbines (and turbomachines in general)
Specific rotational speed

## Slide 3: 2.1. Description and classification
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
Hydraulic machines – machines in which the fluid, while passing through them, exchanges mechanical energy with the moving parts of the machines. In this process, the compressibility of the fluid does not play a role in the energy exchange. Therefore, typically, the fluids that pass through hydraulic machines are liquids, most commonly water, which is where their name originates.
Driving hydraulic machines - machines in which the fluid imparts energy (hydraulic turbines)
Working hydraulic machines - machines that impart energy to the fluid (pumps for liquids and fans for gases)
Based on their construction: blade machines and volumetric machines.
Blade machines, also known as hydraulic turbines, have a rotating working element called a runner, which acts as a profiled circular grid through which the fluid continuously flows, exchanging energy.
Volumetric machines, have reciprocating pistons as their working elements. These pistons move periodically in a linear or circular motion, exchanging energy with limited fluid volumes.
Blade machines and volumetric machines can be used as both driving and working machines.

## Slide 4: 2.1. Description and classification
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
Hydraulic or water turbines are turbomachines in which the available potential and kinetic energy of water is converted into mechanical work through the turbine impeller. The impeller consists of specially designed blades, which are attached to a disk, and the disk is in turn attached to the turbine shaft. Typically, the turbine drives the rotor of a generator to generate electricity in hydroelectric power plants. The coupling of the water turbine and the electric generator is referred to as the aggregate (power unit) of the hydropower plant. In many cases, the rotors of the hydro turbine and the electric generator are located on the same shaft, allowing the conversion of mechanical energy from the turbine's rotation into electrical energy without the need for additional mechanisms.
Hydroturbines of any type consist of three main elements (functional units):
Water supply components or the flow passage, which directs the water to the desired direction and in sufficient quantity towards the turbine impeller.
Rotor (turbine impeller) where the kinetic energy of the water is converted into pressure, that is, mechanical energy.
Water discharge components or the draft tube, which allows the water to exit from the impeller back into the watercourse - discharge structures.

## Slide 5: 2.1. Description and classification
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
According to the working principle, water turbines are divided into:
Impulse or free-jet turbines, and
Reaction or pressure turbines.
Impulse turbines – turbines that utilize only the kinetic energy of water. In these turbines, the water pressures at the inlet and outlet of the turbine impeller are equal to atmospheric pressure. The Pelton turbine is the only turbine that falls into this category.
In reaction turbines, both the pressure and kinetic energy of water are utilized, and the pressure at the inlet of the turbine impeller is higher than the pressure at the outlet. The group of reaction turbines includes the Francis turbine, Kaplan turbine, propeller turbine, horizontal-axis turbine, and diagonal turbine.

## Slide 6: 2.1. Description and classification 2.1.1. Pelton turbine
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
These turbines are suitable for high heads and low flows.
Scheme of a Pelton turbine
Pelton turbine with multiple nozzles and turbine impeller

## Slide 7: 2.1. Description and classification 2.1.1. Pelton turbine
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
Pelton turbines can have 1, 2, or 4 nozzles and 1 or 2 turbine wheels.
Based on the position of the shaft, all turbines are divided into two groups:
Horizontal, and
Vertical.
Pelton turbines can be designed with a horizontal or vertical shaft, depending on spatial and operational conditions.
Construction schemes of Pelton turbines

## Slide 8: 2.1. Description and classification 2.1.2. Francis Turbine
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
The Francis turbine is a reaction turbine because it exchanges the pressure and kinetic energy of water within the turbine. Water enters the turbine radially and exits axially, which is why these turbines are also known as radial or radial-axial turbines.
They are used for heads H=20-400 m (e=200-4000 J/kg) and various power outputs ranging from 1 MW to 250 MW or more.
Scheme of a Francis turbine
Illustration of a Francis turbine

## Slide 9: 2.1. Description and classification 2.1.2. Francis Turbine
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
The main dimensions of the turbine are determined using a series of statistical and empirical indicators. The primary among them are the so-called velocity coefficients, which represent ratios between any velocity in the flow passage and the theoretical velocity . These velocity coefficients are obtained from the basic parameters of each turbine (, , and ).
Flow in the closed position (a) and in the open position (b) of the guide vane blades in a Francis turbine

## Slide 10: 2.1. Description and classification 2.1.3. Propeller and Kaplan turbines
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
These turbines are both axial and reaction turbines and are used for relatively small heads (H=3-60 m, or e=30-600 J/kg) and high flows.
According to the working principle, this turbine does not differ from the Francis turbine.
Scheme of Kaplan turbine
Vertical Kaplan Turbine

## Slide 11: 2.1. Description and classification 2.1.4. Horizontal axis turbine
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
Horizontal axis turbines are increasingly being used, which are more favorable than vertical turbines for low heads. Horizontal turbines have the following advantages:
Higher efficiency and greater capacity,
For the same power, the diameter of the runner is smaller compared to vertical turbines,
Provide an opportunity for a very simple construction of the plant,
The flow passage has a much simpler form - almost linear.
Horizontal axis turbines are predominantly used in capsules, units where the generator is housed in a closed metal capsule with a favorable shape for flow conditions, located in the flow path of the turbine. The flow passage is almost linear, which is why they are also called pipe turbines (bulb turbines). They are designed for very low heads up to 20 m, approximately 15-200 J/kg.
Sometimes these aggregates are located in the water course, so they are called submerged.

## Slide 12: 2.1. Description and classification 2.1.4. Horizontal axis turbine
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
Bulb turbine

## Slide 13: 2.1. Description and classification 2.1.4. Horizontal axis turbine
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
There are solutions of horizontal axis turbines where the generator rotor is designed as a crown on the runner of the turbine. These turbines are also known as straight-flow turbines.
This configuration achieves the most efficient form of the flow passage, which, as in the case of bulb turbines, is in the form of a straight tube. Such turbines are used in run-of-river power plants with abundant water resources and low heads, or as turbines for tidal power generation. In the latter case, the blades are designed in such a way that the turbine can operate in both directions of water flow.
Straight-flow turbine

## Slide 14: 2.1. Description and classification 2.1.5. Diagonal turbine
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
Solutions that enable dual regulation for significantly high heads with a large number of blades – the proposal of Kvatovskij, diagonal turbines were developed, but they were also developed by the English engineer Deriaz, and are often referred to as Deriaz turbines. Later, other companies also developed similar designs.
Diagonal turbine
Runner of a diagonal turbine

## Slide 15: 2.1. Description and classification 2.1.5. Diagonal turbine
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
Diagonal turbines are often constructed as reversible units, meaning they can operate both as turbines and as pumps, achieving a high level of efficiency in both cases. Reversible units are used in reversible (pumped-storage) hydro power plants, where they operate as turbine units, generating and supplying electrical energy to the grid during peak energy demand, and as pumps during periods of low electricity demand. In pump mode, they draw energy from the grid and transfer water from the lower reservoir to the upper reservoir, where it is stored and can be used during peak load periods.