## Slide 1: Modern Hydro Power Plants
Prof. Dr.sc. Gordana Janevska

## Slide 2: Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
Description and classification
  Pelton turbine
  Francis Turbine
  Propeller and Kaplan turbines
  Horizontal axis turbine
  Diagonal turbine
Flow through the runner in reaction turbines
Basic energy equation for turbines (Euler's equation)
Similarity in hydroturbines (and turbomachines in general)
Specific rotational speed

## Slide 3: 2.2. Flow through the runner in reaction turbines
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
Stream surface and streamline (a), flat (b) and circular (c) profile grid
The term "blade grid" is used to facilitate the study of fluid flow through the turbine by allowing the spatial trajectories of fluid particles to be drawn in a plane. Specifically, fluid particles travel through the working space of the turbine along trajectories that lie on stream surfaces obtained by rotating the meridional streamline around the axis of rotation of the turbine. In general, the meridional streamline is a curved line, and its rotation forms a curved surface. In axial-flow machines (axial turbine or pump), the stream surfaces are cylinders, and the streamlines lie on the surfaces of these cylinders. By cutting one of these cylinders along one generatrix and opening it along the circumference, a series of profiles is obtained, formed by the penetration of the blades through the cylinder's circumference. A flat profile grid is obtained by extending this image on one side and on the other side. If the turbine is radial, the stream surface is a spatial plane. The blade penetration into the stream plane results in a circular profile grid.

## Slide 4: 2.2. Flow through the runner in reaction turbines
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
When studying the movement of the fluid through the impeller, that movement is considered as complex – consisting of two movements: relative and transfer. The sum of relative and transfer motion constitutes absolute motion.
The fluid approaches the blades of the turbine with a relative velocity and flows past them with a relative velocity , which constantly changes in direction and magnitude. The blades move with a peripheral velocity , while the velocity at which the fluid impacts the blades (the velocity of the fluid particles relative to the stationary surroundings) represents the absolute velocity .
Velocities and trajectories of water movement in the interblade channels of the runner
(0 – place of undisturbed flow immediately before the entrance to the channel of the runner, 1 – place at the inlet edge of the runner blades, 2 – place at the outlet edge of the runner blades, 3 – place of undisturbed flow immediately after the exit from the channel)
The absolute velocity is obtained by vector addition of the transfer (peripheral) velocity and the relative velocity . Accordingly, the vectors of velocities , and form velocity triangles at the corresponding points on the blades.

## Slide 5: 2.3. Basic energy equation for turbines (Euler's equation)
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
In order to determine the dependencies for the hydrodynamic action and energy exchange between the vane circuit (runner) of the hydraulic turbine and the flow of water through it, a radial vane circuit in the plane of flow of an ideal fluid is considered.
Flow through a rotating blade circuit (runner)
For an elementary particle with mass , where in kg/s is the mass flow rate, the momentum will be , and the conservation of momentum will be:
At the inlet:
At the outlet:
where and are the distances from the attack lines of velocities and to the axis of rotation, and are the inlet and outlet radii of the circuit, and and are the angles that the absolute velocities and make with the direction of the peripheral velocity.

## Slide 6: 2.3. Basic energy equation for turbines (Euler's equation)
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
internal power
is the theoretical specific energy of the circuit and has the dimension J/kg
the fundamental energy equation - Euler's equation for turbines. It is valid for all turbo machines in general. However, for working hydraulic machines (pumps, fans), where the flow is in the opposite direction compared to turbines, the signs on the right side of the equation will be reversed.
For axial turbo machines, where the fluid flow is parallel to the axis of rotation of the impeller, it will be: , , and the equation becomes:

## Slide 7: 2.4. Similarity in hydroturbines (and turbomachines in general)
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
The main parameters characterizing hydro turbines (water turbines) and hydraulic turbo machines in general are the volumetric flow rate [m3/s] or mass flow rate [kg/s] , specific energy [J/kg] and the rotational speed [s-1] or angular velocity [s-1] of the impeller.
With given , and it is not possible to analytically determine the main dimensions of the machine, for example, the external and internal diameter of the blade wheel, and so on, using hydraulic laws alone. These difficulties are overcome by using experimental results expressed in tabular form, graphical representations, or through empirical coefficients and relationships. Even with the current state of the theory of blade grids, which employs extensive mathematical apparatus and computer calculations, dimensioning hydraulic turbo machines without using some experimental data is not possible.
To determine the hydraulic characteristics of the machine and verify whether it meets the specified conditions ( , , ), experimental tests are conducted. The theory of similarity provides significant simplifications for these tests, as it allows large and expensive hydraulic turbo machines (especially turbines) to be tested on a reduced model in a laboratory. Necessary modifications can be made to the model until satisfactory results are obtained in terms of the specified and prescribed technical-economic performance indicators.
Additionally, the obtained dimensionless criteria have universal significance for a family (class) of geometrically similar machines. This means that the results obtained from the experiments on the scaled-down model can be applied to the full-scale machine of the same geometric shape. Thus, the theory of similarity plays a crucial role in the design and optimization of hydraulic turbo machines, enabling cost-effective and efficient solutions.

## Slide 8: 2.4. Similarity in hydroturbines (and turbomachines in general)
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
For hydraulic similarity, it is necessary to maintain geometric, kinematic, and dynamic similarity of the machines.
Geometric similarity involves the proportionality of all relevant dimensions of similar machines.
Kinematic similarity relates to the similarity of flow patterns within the machine, i.e., the proportionality of all velocities at corresponding points while preserving their directions. This similarity implies that the velocity triangles for corresponding flow points in similar machines remain similar.
Dynamic similarity requires the proportionality of forces acting at corresponding points on the machines. This similarity is expressed through the equality of dimensionless numbers such as Reynolds number (), Froude number () and Strouhal number (), where is velocity, is length, and is rotational speed.
In reality, it is not possible to achieve complete similarity according to all criteria for similarity during modeling. Therefore, the most important aspects to satisfy are geometric similarity, kinematic similarity, and Reynolds' law.
Model testing of hydraulic turbo machines is conducted with approximate similarity, focusing on maintaining geometric and kinematic similarity, i.e.
is the coefficient of velocity similarity

## Slide 9: 2.4. Similarity in hydroturbines (and turbomachines in general)
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
The task is to express the velocity ratios in terms of the basic parameters of the machine: , and . For example, from the peripheral velocity ratio, it is:
where is the coefficient of dimension similarity.
the law of kinematic similarity for hydraulic turbo machines and must be fulfilled during modeling, along with geometric similarity and boundary conditions.
Due to the failure to satisfy Reynolds' law, dynamic similarity is not fulfilled for the hydraulic resistances in the machine, which also determines the overall efficiency . Consequently, the measured efficiency of the model, which is a key indicator of the machine's quality, will differ from that of the original. The influence of different Reynolds numbers is taken into account through empirical expressions.

## Slide 10: 2.5. Specific rotational speed
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
the number of rotations can be obtained as:
Objective comparison of two machines with different parameters, , and , is not possible. It can be achieved when comparing models produced with two identical parameter values, while the third one remains for comparison. Typically, J/kg and m3/s are chosen as reference values. Then, from equation
For simplicity, the subscripts are omitted, and is denoted as , called the specific speed (specific rotational speed) or the coefficient of speed relative to flow rate . Hence, the expression becomes:
The comparison can also be made by taking the power kW instead of the flow rate m3/s . In that case, the specific rotational speed is given by
It is called the specific speed (specific rotational speed) relative to power.

## Slide 11: 2.5. Specific rotational speed
Types of hydraulic turbines, constructions, selection of parameters for reaction and impulse turbines
In the field of construction and operation of water turbines, the following numbers are frequently used:
They are referred to as: unit speed, unit power, and unit flow rate because they are numerically equal to the speed of rotation, power, and flow rate of the turbine whose wheel has a diameter m and operates at a head of m .
Accordingly, if the geometry of the best-performing hydraulic turbine with parameters , and is known, all machines with the same specific rotational speed should be designed to have geometric similarity to it. In other words, , or , serves as a criterion for the best geometric form, especially in the energy exchange part - the impeller (runner). Moreover, the specific speed is used to compare individual types of turbines and classify turbine families. It should be noted that the specific speed is calculated and provided for the nominal operating mode of the turbine.