## Slide 1: Modern Hydro Power Plants
Prof. Dr.sc. Gordana Janevska

## Slide 2: Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Main components of hydroelectric power plants and their functions
  Dam
  Intake
  Supply works
  Surge chambers (water chambers)
  Penstock
  Powerhouse
  Generators
  Water Discharge Systems – tailrace
Hydromechanical Equipment
  Trash racks (Gratings)
  Gate Mechanisms
  Equipment for Inlet Structure (Water Intake)
  Dam and Barrier Equipment
  Water Chamber Equipment
  Equipment for the Gate Chamber
  Guidelines for Equipment Selection and Sizing and Weight Estimation
Penstocks
  Types of Penstocks
  The economical (optimal) diameter of the penstock
  Hydraulic Ratios and Sizing Laws
  Guidelines for Dimensioning and Estimation of Weight

## Slide 3: 3.1. Main components of hydroelectric power plants and their functions
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
When constructing a hydroelectric power plant, it is necessary to take into consideration that the operational performance of the plant depends on numerous parameters, such as:
Hydrological,
Meteorological,
Topographical, and
Geological conditions prevailing in the watercourse,
as well as the operational requirements imposed on the facility, specifically the optimal utilization of hydroenergy from the entire watercourse and the existing load diagram.
The choice of the type of hydroelectric power plant depends on a series of factors that influence the rational and economic construction of the plant. Therefore, it is impossible to provide strict rules for selecting the type of plant. Meeting all the necessary conditions requires specific and most favorable solutions for each particular case.
the composition of the hydroelectric power plant includes all the objects and components used for water collection, conveyance, and drainage, for converting mechanical energy into electrical energy, for transformation and distribution of electrical energy, etc.

## Slide 4: 3.1. Main components of hydroelectric power plants and their functions
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Despite the existence of various approaches to this question, in the professional literature, the following main (basic) components of hydroelectric power plants are most commonly analyzed:
Dam,
Reservoir (accumulation),
Water intake (inlet structures),
Headrace or water chamber,
Pressure pipeline,
Powerhouse,
Water turbine,
Generator,
Tailrace structures,
Hydromechanical equipment,
Switchyard,
In certain hydroelectric power plants, some of the mentioned components may be entirely absent, and in some cases, the same component may appear multiple times.

## Slide 5: 3.1. Main components of hydroelectric power plants and their functions 3.1.1. Dam
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Dams (barriers, structures) are constructions that serve multiple purposes:
To redirect the water from its natural flow to the intake of the hydropower plant,
To raise the water level to achieve a greater drop,
To accumulate water for later use.
According to accepted criteria, dams are divided based on their size into:
Large dams, and
Small dams.
Large dams include all dams with a height from the foundation to the crest greater than 15 m, as well as dams higher than 10 m with a crest length greater than 500 m, dams with a volume of the core greater than 100,000 m3, or if the dam needs to allow a water flow greater than 2,000 m3/s. High dams are mainly used for the needs of the power industry.
All other dams are considered small dams. A low dam, which does not significantly change the water level, is also called a weir. Small dams are used for the needs of the power industry but also for other purposes, such as agriculture, creating water reservoirs, tourism, etc.

## Slide 6: 3.1. Main components of hydroelectric power plants and their functions 3.1.1. Dam
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
With regard to the material they are constructed from, dams can be:
Massive dams (constructed from materials like stone, concrete, concrete blocks, reinforced materials, etc.), or
Embankment dams (made of soil, sand, gravel, and rocks...).
In the case of massive dams, there is an upstream part (raised above the riverbed) called the body of the dam, which resists the pressure of the water, and a downstream part, usually in the form of a slab placed on the riverbed, called the spillway.
The choice of dam type depends primarily on the geological composition of the terrain, the materials available for construction, and the economic viability of the construction.
On every dam, external and internal forces act. External forces include the pressure of the water on the upstream side, the pressure of the water at the joint between the foundation and the soil, ice pressure (if ice occurs), pressure from the surrounding soil, and pressure from sediment deposition. Internal forces consist of the dam's self-weight, forces arising due to temperature changes in the concrete, forces due to shrinkage of concrete...
Large dams, either massive or embankment, are mostly used for the needs of the power industry. Today, massive dams are almost exclusively constructed of concrete. In the case of concrete dams, waterproofing is achieved by selecting the type/brand of concrete.

## Slide 7: 3.1. Main components of hydroelectric power plants and their functions 3.1.1. Dam
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Massive concrete dams are divided into several types:
Gravity dams,
Arch dams,
Arch-gravity dams,
Buttress dams
And their combinations.
Gravity dam

## Slide 8: 3.1. Main components of hydroelectric power plants and their functions 3.1.1. Dam
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Arch dam
Sketch of an arch-gravity dam

## Slide 9: 3.1. Main components of hydroelectric power plants and their functions 3.1.1. Dam
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Sketch of the buttress dam
Embankment dam

## Slide 10: 3.1. Main components of hydroelectric power plants and their functions 3.1.1. Dam
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Devices must be provided to enable the controlled discharge of excess water without causing harm to the areas located upstream and downstream of the dam.
The choice of drainage method for excess water depends on the length of the dam, the type of dam, the possibilities upstream and downstream of the dam, and other factors.
For draining excess water and regulating water levels during high floods, the following methods are used:
Spillways (across the entire dam or through a part of the dam),
Outlets and flow fields within the dam,
equipped with movable barriers that open when the water reaches a certain height. Gates are used to control the water flow during dam discharge.
The capacity of the water drainage devices (spillway structures, outlets, and water discharge through turbines) should be sufficient to prevent flooding of the observed area, ensuring the safe discharge even during the largest possible inflows.

## Slide 11: 3.1. Main components of hydroelectric power plants and their functions 3.1.1. Dam
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Different forms of spillways at massive dams
Segment gates

## Slide 12: 3.1. Main components of hydroelectric power plants and their functions 3.1.2. Intake
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
In order to carry out its function, the intake is designed to collect water from the watercourse or the dam and direct it into the intake structures of the power plant. There are two types of intakes:
Surface intake, and
Subsurface intake.
The surface intake is employed when the water level behind the dam is low, resulting in a relatively constant water level. The flow of water through the intake is regulated using gates and barriers (locks).
Intake above the water surface

## Slide 13: 3.1. Main components of hydroelectric power plants and their functions 3.1.2. Intake
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
When, due to water accumulation during the rainy season for its use in the dry season, the water level significantly varies throughout the year, the intake should be placed below the water level, specifically at the lowest level to which the water recedes. Such an intake is referred to as a subsurface intake.
Subsurface intake

## Slide 14: 3.1. Main components of hydroelectric power plants and their functions 3.1.3. Supply works
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Supply works connect a water intake to the penstock inlet of a hydroelectric plant. Depending on the topography of the terrain where the supply works are installed, available materials, and the operational requirements of the hydroelectric power plant, they can be constructed as:
Canal,
Tunnel, or
A combination of the above two.
The canal can be:
Open channel
Closed conduit
Water conveyance: a) open canal, b) closed conduit

## Slide 15: 3.1. Main components of hydroelectric power plants and their functions 3.1.3. Supply works
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The tunnel can be constructed as:
Gravity tunnel,
Pressure conduit.
In gravity tunnels, water flows freely and does not fill the entire tunnel. Therefore, to change the water flow rate, it requires adjusting the opening of the gate at the intake.
In tunnels under pressure, the water fills the entire cross-section of the pipe, and the water level at the entrance of the tunnel should always be higher than the highest water level inside the tunnel. To change the amount of water supplied to the power plant, no action is required at the intake.
Gravity tunnel for water conveyance
Pressurized tunnel for water conveyance

## Slide 16: 3.1. Main components of hydroelectric power plants and their functions 3.1.4. Surge chambers (water chambers)
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The surge chamber, or the water chamber, is an expansion chamber located at the end of the water conveyance line, just before the penstock. The function of the water chamber depends on the type of water conveyance.
When the water conveyance is gravity-fed, a surge chamber with sufficient volume is needed to serve as a water reservoir, ensuring an adequate water supply for the turbines in case of unexpected load changes. Its dimensions should be such that it provides enough water to prevent the entry of air into the penstock along with the water.
If the hydroelectric power plant has a pressure conduit for water conveyance, the expansion at the end of that conduit must be designed as a water chamber with specific dimensions. This allows the pressure in the conduit not to exceed the allowable limit after load changes (to avoid water hammer in the pipes or the pressure tunnel) and ensures that the water level does not drop below the highest level at the entrance of the penstock. In this case, the water chamber functions as a valve.
Longitudinal sections of a type of water chamber

## Slide 17: 3.1. Main components of hydroelectric power plants and their functions 3.1.4. Surge chambers (water chambers)
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The water chamber, in fact, is a chamber with a suitable form designed to receive the water surge that occurs in the full accumulation basin in the event of a sudden interruption of the supply and during load changes in the generating units.
The water chamber resolves the phenomenon of water hammer, which is not the subject of discussion here, but still needs to be mentioned. It involves converting the kinetic energy of the water mass during operating maneuvers into potential energy in accordance with the relationship:
𝐿 [m] − length of the penstock,
[m2] − cross-sectional area of the conduit,
∆𝑣 [m/s] − change in water velocity within the conduit,
[m2] − cross-sectional area of the water chamber,
𝑍 [m] − change in water level within the water chamber during the process.

## Slide 18: 3.1. Main components of hydroelectric power plants and their functions 3.1.4. Surge chambers (water chambers)
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The essential data for calculating water hammer includes:
The model of the entire plant from the inlet to the outlet of the water mass,
Inertia masses 𝐺 ∙ 𝐷2 of rotating parts (hydraulic machine and electric generator),
Relevant data of the penstock,
Technical specifications of the hydraulic turbine,
The closure law of the water inlet apparatus (distributor).
The design conditions for the water chamber are complex and depend on the type and role of the power plant in the power system. The primary principle is to provide dimensions that enable all possible operational maneuvers.
In certain cases, for long tailrace tunnels (in power plants with an underground powerhouse), it is necessary to incorporate a bottom water chamber located behind the turbine diffuser, serving a similar function to the upper water chamber.

## Slide 19: 3.1. Main components of hydroelectric power plants and their functions 3.1.5. Penstock
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Penstocks are used to convey water from the surge chamber or water chamber to the turbines. Typically, they are made of steel and special alloys, and for smaller heads, they can be made of concrete or reinforced concrete. Depending on their location, penstocks can be installed on the surface of the terrain or placed inside a tunnel.
The penstock ends with a diverging conduit through which water from the penstock is directed to each of the turbines. Since pressures and velocities are very high in the diverging conduit, it must be dimensioned for the appropriate conditions.
Sketch and picture of a penstock installed on the surface of the terrain

## Slide 20: 3.1. Main components of hydroelectric power plants and their functions 3.1.6. Powerhouse
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The powerhouse serves to accommodate the turbines, generators, control panel, and other auxiliary equipment and machinery for operation, assembly, repairs, and maintenance, as well as to house the personnel.
The type of powerhouse is primarily dictated by topographical and economic reasons. In terms of the location of the powerhouse, there are two main types:
Open-air powerhouses,
Underground powerhouses.
Interior of the powerhouse in a hydroelectric power plant

## Slide 21: 3.1. Main components of hydroelectric power plants and their functions 3.1.7. Generators
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Synchronous generators or alternators are rotating electrical machines that convert mechanical energy from their shaft into electrical energy.
In power plants, three-phase synchronous generators are commonly used with a frequency of 50Hz (in Europe) or 60Hz (in the USA and Canada).
The essential nominal data required for the analysis of the generator are as follows:
Rated (nominal) voltage ,
Rated (nominal) power ,
Rated (nominal) power factor cos ,
Number of revolutions (rotational speed) of the rotor n.
In addition to these parameters, in some cases, specific requirements need to be specified, such as the synchronous reactance size, voltage regulation range, torque, number of phases, stator winding connections, etc., depending on the network requirements for the generator.

## Slide 22: 3.1. Main components of hydroelectric power plants and their functions 3.1.7. Generators
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Structurally, synchronous generators consist of two main parts:
Stator - a stationary part with slots that accommodate a three-phase winding,
Rotor - a rotating assembly with electromagnets to which a direct current is supplied through contact rings on the rotor shaft and brushes that make contact with them.
In practice, two main types of synchronous generators are used:
Synchronous generator with salient poles or hydro generator, and
Synchronous generator with a cylindrical rotor or turbo generator.
Installation of the rotor on the hydro generator
AC synchronous electric hydro generator with four pairs of poles on the rotor

## Slide 23: 3.1. Main components of hydroelectric power plants and their functions 3.1.7. Generators
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Due to the electrical, mechanical, and thermal stresses to which the insulation of the synchronous generator is exposed during operation, various defects can occur in its operation. In addition to defects, there are hazardous operating conditions that can arise during generator operation, which may lead to defects if not prevented.
Considering the significant value of the generator in terms of its procurement cost and the potential damages incurred in the event of a failure to produce electrical energy, it is necessary to ensure protection that will:
prevent damage to the generator,
or limit the damage in the event of an unavoidable defect.
The protection devices for the generator can be divided into:
Devices that act after a defect occurs in the protected generator, and
Devices intended to protect the generator from external factors causing defects.
When deciding on the type and degree of protection, it is advisable to assess the probability of defects occurring in the generator.

## Slide 24: 3.1. Main components of hydroelectric power plants and their functions 3.1.8. Water Discharge Systems – tailrace
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The water discharge at hydro power plants is carried out through either:
a tunnel or
a canal.
The design and construction of the water discharge canal are similar to the water intake canal. Its main purpose is to carry the water that has already transferred its energy to the turbine and return it back to the river or waterway, or in some cases, it can also serve as a supply channel to direct the water towards the intake of the next hydro power plant.
Water discharge at the hydro power plant