## Slide 1: Modern Hydro Power Plants
Prof. Dr.sc. Gordana Janevska

## Slide 2: Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Main components of hydroelectric power plants and their functions
  Dam
  Intake
  Supply works
  Surge chambers (water chambers)
  Penstock
  Powerhouse
  Generators
  Water Discharge Systems – tailrace
Hydromechanical Equipment
  Trash racks (Gratings)
  Gate Mechanisms
  Equipment for Inlet Structure (Water Intake)
  Dam and Barrier Equipment
  Water Chamber Equipment
  Equipment for the Gate Chamber
  Guidelines for Equipment Selection and Sizing and Weight Estimation
Penstocks
  Types of Penstocks
  The economical (optimal) diameter of the penstock
  Hydraulic Ratios and Sizing Laws
  Guidelines for Dimensioning and Estimation of Weight

## Slide 3: 3.2. Hydromechanical Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The turbine and the generator with their auxiliary devices as well as the switchgear and other electrical equipment make up the electromechanical equipment of the hydroelectric plant. In addition, the hydromechanical equipment of the power plant should be listed, including: the spillway equipment, the foundation outlet and inlet structure, the tunnel equipment, the water chamber, the gate chamber and the drainage channel. A pre-turbine gate is installed in front of the turbine, depending on the type of turbine and its characteristics.
The hydromechanical equipment is a complex of machinery and devices integrated into the system of hydropower plants and hydrotechnical facilities, with the primary task of controlling and regulating the technical process and protecting the plant from failures and damages.
The main tasks of the hydromechanical equipment are as follows:
To ensure and regulate an adequate flow of water in accordance with the needs of the power plant during normal operation,
To quickly close and stop the flow of water in the event of a defect in any of the intake structures,
To prevent foreign objects from entering the intake structures of the power plant, thereby avoiding blockages or damage.

## Slide 4: 3.2. Hydromechanical Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Hydro-mechanical equipment, based on its primary tasks and purposes, can be divided into the following components:
Gratings (trash racks) that should prevent the entry of large debris and various solid objects into the flow part of the turbine (waste material, leaves, ice during winter, etc.).
Gate Mechanisms (shut-off devices) – hydromechanical elements that are used to open and close the penstock (pipe or conduit), that is, to control water flow using gates or valves (quantitative regulation), in order to determine the power at which the turbine operates.
Devices for manipulation of hydromechanical equipment and auxiliary devices, such as various cranes, hoists, etc., with which hydromechanical equipment is manipulated during operation, or individual components are manipulated during overhauls. Auxiliary devices include all equipment designed to ensure the efficient operation of the hydro-mechanical equipment. This category also includes equipment for cleaning grates (trash racks) from accumulated waste materials, various hooks, holders and clamps that allow various connections, etc.
Since there is no universal scheme of a hydropower plant (there is only a principle scheme), the choice of hydromechanical equipment depends on the specific circumstances. Therefore, it varies from one facility to another, as each solution is unique and one-of-a-kind in itself.

## Slide 5: 3.2. Hydromechanical Equipment 3.2.1. Trash racks (Gratings)
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The proper and successful operation of aggregates and plants, as a whole, depends on the purity of the water passing through the turbine. Trash racks (gratings) are used to remove solid floating objects, ice and other debris that can clog flow passages and cause turbine failure or major breakdowns and other damage.
Racks are installed at the beginning of the hydroenergy system, specifically in the water intake and in front of the turbine itself if the derivation channel is open, as it can also accumulate impurities (leaves, branches, etc.).
Depending on where the grating is installed and according to the method of capturing water in the water intake, the grating can be either surface or submerged (deep).
Vertical Grating at the Water Intake of a Reservoir

## Slide 6: 3.2. Hydromechanical Equipment 3.2.1. Trash racks (Gratings)
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The rack (grating) typically consists of vertical bars that are placed at a certain distance from each other. Depending on its quality and purpose, the grating (rack) can be:
Fine: This type of grating is installed as the first element in the intake structures, typically to filter out smaller debris and impurities.
Coarse: Coarse gratings are installed at outlets and flow passages with a larger profile, mainly to filter out larger debris and impurities.
The rack is always in operation (in contact with water), except when the annual overhaul is done, when the turbine units are not in operation. Then, instead of the rack, a maintenance gate is lowered into the same opening. This gate is used to shut off the water flow to the turbine, allowing necessary maintenance work to be carried out without interruption.

## Slide 7: 3.2. Hydromechanical Equipment 3.2.2. Gate Mechanisms
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Gate mechanisms are devices used to open or close hydraulic structures and regulate water flow. They are generally divided into two main groups:
Sluice Gates (Sluices): These are used for opening, closing, and regulating flow in open channels and reservoirs.
Gate Valves (Valves): These are used for opening, closing, and regulating flow in pipelines.
Gate valves for pressurized pipelines in hydroenergy facilities, such as hydroelectric power plants, are divided into:
Flat Gates (Flat Sluices): These are flat gates used to control water flow.
Butterfly Valves: These are gate valves shaped like butterfly wings.
Spherical (Ball) Valves: These are gate valves in the shape of spheres or balls.
Needle Valves (Johnson Valves): These are gate valves with needle-like mechanisms.

## Slide 8: 3.2. Hydromechanical Equipment 3.2.2. Gate Mechanisms
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Flat Gates (Flat Sluices)
Sluice Gates have a wide range of applications in all fields of the energy sector, i.e., wherever fluids are transported, regardless of whether it's liquid, steam, or gas. In hydroelectric installations, they are used in low-capacity hydroelectric power plants, which have low flow rates and operate individually. A characteristic feature of gate valves is that the gate within the valve housing moves only in a translational manner, maintaining high pressures through significant friction in the guides. They are simple in design, relatively inexpensive, and effectively shut off the flow of water.
Basic sketches and pictures of Flat Sluices

## Slide 9: 3.2. Hydromechanical Equipment 3.2.2. Gate Mechanisms
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Butterfly Valves
The primary purpose of butterfly valves is to open and close the pressure pipeline, but they have also found applications as flow regulators. In special cases, they are used as protective and safety devices for pressure pipelines in the event of emergencies (check valves in pump installations). These are shut-off devices designed for closing or opening the cross-section of the pipeline.
Their drawback is that they cannot seal well, meaning due to the need for manipulation, there must be a certain distance between the butterfly (the closing plate) and the pipe through which water flows at high pressures.
Appearance and Sketch of a Butterfly Valve

## Slide 10: 3.2. Hydromechanical Equipment 3.2.2. Gate Mechanisms
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Spherical (Ball) Valves
Spherical valves for pressure pipelines find the widest application in water turbines in hydroelectric power plants as pre-turbine valves because they perform very well in closing the flow. The main advantage of spherical valves is that in the fully open position, they represent a continuation of the pipeline, so hydraulic losses in them are practically zero, and the flow of water undergoes no changes. Spherical valves are only used for fully open and fully closed positions, and that for rapid opening and closing. Always, an air valve is installed behind them to remove air from the spiral when it is filled with water and to vent atmospheric air when emptying the spiral.
Principle sketch of a Spherical Valve

## Slide 11: 3.2. Hydromechanical Equipment 3.2.2. Gate Mechanisms
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Needle Valves
Due to their excellent properties, needle valves are used especially in pipelines operating under high pressures, most commonly as pre-turbine valves. Due to the complexity of their construction, they are quite expensive. Their drawbacks are their size and large mass. The masses of the butterfly, spherical, and needle valves at the same dimensions are in a ratio of 1:2:3. Needle valves have excellent hydraulic characteristics: their closing element aligns well with the water flow, there are no major sealing problems, they are easy to operate, and it's easy to enable any position (and thus the flow of water). These valves have the widest application as control valves in pipelines where flow changes during operation. In this case, the closing element can take various positions.
Principle sketch of a needle closure Needle Valve

## Slide 12: 3.2. Hydromechanical Equipment 3.2.3. Equipment for Inlet Structure (Water Intake)
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The equipment for the inlet structure (water intake) depends on the type of structure and its characteristics.
For river and canal hydroelectric power plants, the inlet structure (water intake) is equipped with:
Inlet grating (trash rack) with a cleaning device (trash rack cleaner)
Timber stop logs.
Inlet Grate

## Slide 13: 3.2. Hydromechanical Equipment 3.2.3. Equipment for Inlet Structure (Water Intake)
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
In medium-pressure and high-pressure hydroelectric power plants, where significantly lower flow rates are handled, the dimensions of the inlet structure are considerably smaller from a hydraulic perspective. As a result, the inlet grates are also much smaller in size. Instead of timber stop logs as a closing mechanism, flat gates with hydraulic drive are used. The hydraulic drive system typically involves pressurized oil supplied by a group of pump-motor units along with the necessary auxiliary equipment.
The construction of the grates (trash racks) can be either inclined or vertical. Vertical metal grates are typically made from shaped steel, while horizontal or sub-horizontal grates are constructed using profiled and shaped iron. The grates, timber stop logs, and vertical columns, which are usually concrete, must undergo hydraulic shaping. The spacing of the grates in hydroenergy facilities depends on the type of hydraulic structure.
In complex designs of inlet structures, experimental hydraulic model tests are often conducted to examine and prevent the occurrence of vortex flow in front of and around the grates.

## Slide 14: 3.2. Hydromechanical Equipment 3.2.3. Equipment for Inlet Structure (Water Intake)
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Grate (Trash Rack) Scheme
a) Upstream side of the grate, b) Cross-section A - A, timber stop logs made of profiled iron with concrete filling oriented in the direction of the water flow c) Cross-section B - B, horizontal timber stop logs,
1. Vertical column, 2. Horizontal timber stop log, 3. Grate bars, 4. Bar slide, 5. Divider

## Slide 15: 3.2. Hydromechanical Equipment 3.2.3. Equipment for Inlet Structure (Water Intake)
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Various Types of Mechanical Cleaners for Grates (Trash Rack Cleaners)
a) Cleaning machine with a bucket, b) Bucket, c) Grabber, d) Grapple, e) Forked grabber, f) Water bulldozer,
g) Pneumatic grabber type "polyp"
1. Upper fork, 2. Lower fork, 3. Кnife, 4. Brush, 5. Rake

## Slide 16: 3.2. Hydromechanical Equipment 3.2.3. Equipment for Inlet Structure (Water Intake)
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Inlet structures (water intakes) and hydro-mechanical equipment are categorized based on the construction of hydroelectric plants:
Inlet structures (intakes) for run-of-river low-pressure hydropower plants: These are designed for hydroelectric plants that utilize low-pressure flow from rivers.
Inlet structures (intakes) for impoundment hydropower plants: These are designed for hydroelectric plants that store water in a reservoir before using it for power generation.
Inlet structures (intakes) for diversion (gravity and pressure) hydro power plants: These are designed for hydroelectric plants that divert water from its natural course to generate power, either by gravity or pressure.
Additionally, there is a special category for pump stations, where water intake, for energy, water management, or supply purposes, is carried out using pumps.

## Slide 17: 3.2. Hydromechanical Equipment 3.2.3. Equipment for Inlet Structure (Water Intake)
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Inlet structures for run-of-river low-pressure hydropower plants
Inlet structures for run-of-river low-pressure hydropower plants are an integral part of the dam. Each unit has a separate water intake and its own inlet structure.
These inlet structures are equipped with:
An inlet grate (trash rack) with a cleaning device (trash rack cleaner).
Auxiliary timber stop logs and main flat gates.
Inlet Structures for Low-Pressure Run-of-River Hydropower Plants

## Slide 18: 3.2. Hydromechanical Equipment 3.2.3. Equipment for Inlet Structure (Water Intake)
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Inlet structures for impoundment hydropower plants
When it comes to a reservoir hydroelectric power plant located downstream from the concrete dam, the inlet structure can be designed as a separate object from the dam, it can be located on the dam, or within the dam itself.
Inlet structure with hydromechanical equipment

## Slide 19: 3.2. Hydromechanical Equipment 3.2.3. Equipment for Inlet Structure (Water Intake)
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Inlet Structures of Derivative Hydroelectric Power Plants
Inlet structures for the water diversion of pressured derivations are typically equipped with:
Fine grates, which can be vertical or inclined,
Cleaners,
Auxiliary and main gates and valves,
Aeration pipes or windows,
Vehicle inlets through a removable section of the grate or a vertical window.
Inlet Structure, Supply Tunnel of a Pressured Derivation

## Slide 20: 3.2. Hydromechanical Equipment 3.2.4. Dam and Barrier Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Spillway
The equipment for the spillway primarily depends on the type of dam and the amount of water that needs to be released.
In the case of river and canal power plants, segmented gates with an overflow section are most commonly used. The overflow section is used for fine level regulation, while segmented gates are used to release larger quantities of water. These gates are a more cost-effective solution compared to other types of gates, considering their weight, cost, and the fact that they have a simple operation.
Segmented gate with an overflow section and surface overflow section

## Slide 21: 3.2. Hydromechanical Equipment 3.2.4. Dam and Barrier Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Spillway
For embankment barriers, spillway is managed through a separate tunnel, and the equipment at the inlet can vary significantly, depending on hydraulic and construction requirements. A common choice is an overflow gate with a classic design or circular overflow construction. If the spillway is managed with surface concrete construction, the inlet section is equipped with segmented gates.
The gates used at spillways can be divided into two categories:
Gates supported on the sides:
  Beam gates,
  Plate gates,
  Segmented gates,
  Roller gates,
  Hook gates.
Gates supported at the top:
  Sector gates,
  Flap gate,
  Circular gates,
  Cover gates.

## Slide 22: 3.2. Hydromechanical Equipment 3.2.4. Dam and Barrier Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Beam gate
Plate gate

## Slide 23: 3.2. Hydromechanical Equipment 3.2.4. Dam and Barrier Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Segmented gate
Roller gate

## Slide 24: 3.2. Hydromechanical Equipment 3.2.4. Dam and Barrier Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Sector gate
Flap gate
Circular gate

## Slide 25: 3.2. Hydromechanical Equipment 3.2.4. Dam and Barrier Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Оutlet in the dam foundation
In the case of reservoir hydroelectric power plants with earthen (stone) dams, the outlet in dam foundation is constructed as a separate tunnel. At the tunnel entrance, a segmental gate is installed in combination with an overflow valve. For solutions with equipment at the tunnel outlet, a sliding plate gate is used.
Sliding gate for a dam foundation outlet

## Slide 26: 3.2. Hydromechanical Equipment 3.2.4. Dam and Barrier Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Оutlet in the dam foundation
In the dam foundation outlet, two types of gates are installed for the continuous release of water from the reservoir for irrigation purposes or other needs. The first type is a needle valve, and the second is a cylindrical valve.
Sketch of a needle valve and a sliding valve

## Slide 27: 3.2. Hydromechanical Equipment 3.2.4. Dam and Barrier Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Оutlet in the dam foundation
There are also butterfly and ball valves that are most commonly used as pre-turbine valves (inlet valves), which are devices for controlling the water supply to the hydropower plant.
Sketches of a Butterfly Valve and a Ball Valve

## Slide 28: 3.2. Hydromechanical Equipment 3.2.4. Dam and Barrier Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Earthen embankment dam with main structures and depiction of the equipment installation location
1 - Inlet structure of the foundation outlet, 2 - Auxiliary gate of the foundation outlet, 3 - Regulating gate of the foundation outlet, 4 - Inlet structure of the intake tunnel for the powerhouse, 5 - Gatehouse with actuating mechanism, 6 - Control gallery, 7 - Inlet structure for the overflow, 8 - Overflow tunnel, 9 - Inlet structure for the overflow, 10 - Powerhouse

## Slide 29: 3.2. Hydromechanical Equipment 3.2.4. Dam and Barrier Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The gates at the foundation outlets and inlets control (open/close) the pressurized flow. They are also used in inlet tunnels, pipelines, which can be under pressure and have a free water surface behind the gate.
Gate at the foundation outlet
Butterfly valve

## Slide 30: 3.2. Hydromechanical Equipment 3.2.4. Dam and Barrier Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Ball valve
Conical valve
Needle valve
Circular-cylindrical valve

## Slide 31: 3.2. Hydromechanical Equipment 3.2.5. Water Chamber Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The equipment for the water chamber consists of an inlet tunnel, as well as some main and auxiliary circular profiles within the space of the water chamber. If the water chamber is used for two stages of construction, for example, for two inlet tunnels between the two tunnels, plate gates (valves) are installed at the junction to the common chambers.
If the chamber is connected to the outside surface of the field, the entrance should be equipped with grates to protect against the penetration of unwanted objects into the water chamber system, including the supply tunnel and the penstock.
Water chambers can be divided into three groups as follows:
Water chambers at the inlet of water with a free water surface,
Water chambers at the pressurized inlet of water,
Water chambers at the pressurized outlet of water.
The main task of the water chambers is to meet the variability of the load depending on the requirements of the power system, of which they are an integral part.

## Slide 32: 3.2. Hydromechanical Equipment 3.2.5. Water Chamber Equipment
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Water Chamber and Inlet Structure of the Penstock
1. Diversion channel, 2. Water chamber, 3. Maintenance gate guides, 4. Inlet section, 5. Air vent pipe, 6. Safety plate gate, 7. Penstock of the turbine, 8. Grating

## Slide 33: 3.2. Hydromechanical Equipment 3.2.6. Equipment for the Gate Chamber
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The gate chamber or gate operator chamber must be equipped with butterfly safety valves for protection in case of an accident in the penstock. The arrangement of the equipment and the detailed characteristics of the gates depend on hydraulic and other requirements .
Cross-section through the gate chamber of a high-pressure hydro power plant

## Slide 34: 3.2. Hydromechanical Equipment 3.2.7. Guidelines for Equipment Selection and Sizing and Weight Estimation
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
When selecting equipment for hydroenergy facilities, the following should be considered as a priority:
Hydraulic requirements
Economic feasibility of the structure.
The selection of one of the types of gates for specific conditions is a complex issue, and there is no fixed rule for this choice. Instead, a series of technical and economic analyses should be conducted on a case-by-case basis to make a decision.
The basis for sizing includes: hydraulic pressure and conditions for the steady state, as well as conditions for various operational situations, such as unidirectional pressure, opening under equal pressure, and opening under full pressure from one side of the gate.

## Slide 35: 3.2. Hydromechanical Equipment 3.2.7. Guidelines for Equipment Selection and Sizing and Weight Estimation
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Sizing of the gate
For plate gates, the formula for calculating the force due to water pressure (in Newtons, N) is as follows:
– density of water, [kg/m3]
– acceleration due to gravity, [approximately 9.81 m/s²]
– difference in water level height and the gate axis, [m]
– surface area of the gate, [m2].
For segmented gates (Fig. 79), the formula for calculating the force due to water pressure (in Newtons, N) is as follows:
The drag force () is

## Slide 36: 3.2. Hydromechanical Equipment 3.2.7. Guidelines for Equipment Selection and Sizing and Weight Estimation
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Mass of Surface Gate
Mass of Discharge Gate