## Slide 1: Modern Hydro Power Plants
Prof. Dr.sc. Gordana Janevska

## Slide 2: Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Main components of hydroelectric power plants and their functions
  Dam
  Intake
  Supply works
  Surge chambers (water chambers)
  Penstock
  Powerhouse
  Generators
  Water Discharge Systems – tailrace
Hydromechanical Equipment
  Trash racks (Gratings)
  Gate Mechanisms
  Equipment for Inlet Structure (Water Intake)
  Dam and Barrier Equipment
  Water Chamber Equipment
  Equipment for the Gate Chamber
  Guidelines for Equipment Selection and Sizing and Weight Estimation
Penstocks
  Types of Penstocks
  The economical (optimal) diameter of the penstock
  Hydraulic Ratios and Sizing Laws
  Guidelines for Dimensioning and Estimation of Weight

## Slide 3: 3.3. Penstocks 3.3.1. Types of Penstocks
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
With today's technological capabilities and in accordance with field conditions, including geological and topographical factors, the following types of pressure pipelines (penstocks) are constructed:
Openly placed,
Freely laid in trenches,
Placed in surface excavations and backfilled with soil or material obtained from excavation,
Concrete-lined trenches or channels.
Penstocks terminate with distribution pipelines, which are primarily constructed as freely laid in trenches or as concrete-lined trenches or channels. In the case of pipelines concreted in channels, this can be used for partial absorption of internal forces.

## Slide 4: 3.3. Penstocks 3.3.1. Types of Penstocks
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Example of an Open Steel Pressure Pipeline

## Slide 5: 3.3. Penstocks 3.3.1. Types of Penstocks
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Example of a vertically installed concrete-lined steel pressure pipeline in a trench

## Slide 6: 3.3. Penstocks 3.3.2. The economical (optimal) diameter of the penstock
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
After selecting the general concept of the hydroelectric power plant (or pumping hydro plant or pumping station) and defining the installed flow rate, the choice of the pipeline type is made. For this purpose, extensive technical-economic analyses are required, with the most important being the selection of the economical diameter.
The working pressure in the penstock is
Investment costs, and consequently annual costs, increase with the increase in diameter, while annual costs due to energy losses decrease with the increase in diameter.
The energy losses consist mainly of losses due to friction.
[m/m] – head losses in the pipeline (Darcy);
is the friction coefficient;
[m/s] – average water flow velocity in the pipeline

## Slide 7: 3.3. Penstocks 3.3.2. The economical (optimal) diameter of the penstock
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
[m3/s] –relevant flow rate, flow rate at nominal load
Considering the working water duration curve, there is the relationship:
[h] – time of application of the relevant flow rate or annual number of working hours reduced to the relevant flow rate;
The thickness of the pipeline walls
[Pa=N/m2] – allowable stress of the steel of the pipeline

## Slide 8: 3.3. Penstocks 3.3.2. The economical (optimal) diameter of the penstock
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Tthe investment costs per meter of pipeline length will be:
[kg/m3] – density of the steel of the pipeline;
– cost of the installed pipeline;
–factor for smooth pipe accessories (connectors, aligners, etc.)
Annual construction costs are given by:
– capital cost factor (relative or percentage value)

## Slide 9: 3.3. Penstocks 3.3.2. The economical (optimal) diameter of the penstock
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Friction losses
Annual losses costs
– cost per kWh of electricity, i.e. lost energy (power × time = energy);
– system efficiency.
The total annual operating costs
The minimum cost law

## Slide 10: 3.3. Penstocks 3.3.2. The economical (optimal) diameter of the penstock
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
The calculation using equation
can also be realized graphically, and it is necessary to be conducted in segments. In precise calculations, it is necessary to take into account the different tariffs for electrical energy based on the price of guaranteed capacity in the system.
The economic (optimal) diameter should be calculated using an empirical formula, which remarkably coincides with the actually implemented diameters:
[m] – optimal diameter;
[kW] – nominal power of the turbine or pump;
[m] – nominal head of the turbine or pump.

## Slide 11: 3.3. Penstocks 3.3.3. Hydraulic Ratios and Sizing Laws
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Equivalent Pipeline
For the analysis and definition of dynamic phenomena in the water chamber system (surge tank) - pressured pipeline (penstock) - turbine, the concept of an equivalent pipeline is used for the purpose of quick calculations of the basic hydraulic ratios and hydrodynamic parameters.
The total length of the pressured pipelines (penstocks) [m] consists of unequal sections (segments), which are characterized by the following parameters:
length [m]; ;
internal diameter [m] ;
wall thickness [m] ;
cross-sectional area [m2] ;
maximum flow rate in the operating mode [m3/s] at a head [m] of the turbine or head [m] of the pump with the valve fully open;
water flow velocity [m/s] for the respective flow rate ;
velocity of the pressure wave (during rapid closure) for freely placed pressured pipelines

## Slide 12: 3.3. Penstocks 3.3.3. Hydraulic Ratios and Sizing Laws
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Equivalent Pipeline
The velocity of pressure wave propagation for steel pipelines placed in a tunnel with concrete lining
[kg/m3] – density of water;
[da N/m2] –modulus of water elasticity;
[m] – internal diameter of the steel pipe;
[m] – external diameter of the steel pipe; ;
[m] – thickness of the steel walls;
[da N/m2] – Young's modulus of steel elasticity;

## Slide 13: 3.3. Penstocks 3.3.3. Hydraulic Ratios and Sizing Laws
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Equivalent Pipeline
For a reinforced concrete tunnel without steel pipes
[da N/m2] – Young's modulus of concrete elasticity;
[m] – internal diameter of the tunnel;
;
– reinforcement coefficient, where [m2] is the area of the reinforcement, and [m] is the thickness of the concrete lining.

## Slide 14: 3.3. Penstocks 3.3.3. Hydraulic Ratios and Sizing Laws
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Equivalent Pipeline
The real pipeline, consisting of sections with the above characteristics, can be replaced for the necessary analysis and calculations by the so-called equivalent pipeline, which will have the same length and a constant diameter, with the following parameters:
Equivalent velocity [m/s]
Equivalent velocity of wave propagation [m/s]
Equivalent diameter [m]

## Slide 15: 3.3. Penstocks 3.3.3. Hydraulic Ratios and Sizing Laws
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Equivalent Pipeline
When calculating dynamic transient conditions (closing and opening of the water conveyance system, sudden load drops at full load, etc.) for all groups connected to the equivalent pipeline, the following conditions are applied:
The flow rate in the pipeline is equal to the sum of the flows of individual turbines,
The hydraulic power of the entire system is equal to the sum of the powers of individual groups,
The expression for the system is equal to the sum of for individual groups,
the maneuvers with the guide vane should have the same conditions and characteristics for all turbines.

## Slide 16: 3.3. Penstocks 3.3.3. Hydraulic Ratios and Sizing Laws
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Cases of Sudden Changes in Operating Mode
Slow Linear Changes in Operating Mode
If [s] represents the shortest time for closing the water conveyance system (distributor) from 100 to 0, and [s] represents the shortest time for opening the water conveyance system (distributor) from 0 to 100, then all possible linear changes in the operating mode (maneuvers) of the conveyance system can be defined as 'slow' if the following condition is met:
In the most critical cases during closure, with sufficient approximation, the largest direct increase in pressure in percentage of the dynamic pressure [m] at the end of the lower part of the conduit can be determined using the expression (MICHAUD):

## Slide 17: 3.3. Penstocks 3.3.3. Hydraulic Ratios and Sizing Laws
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Cases of Sudden Changes in Operating Mode
Slow Linear Changes in Operating Mode
When opening, it can be assumed that in the most unfavorable (critical) case, there is a direct decrease in pressure in percentage of the dynamic pressure [m] at the end of the lower part of the conduit, can be determined using the expression:
[m] –maximum direct pressure increase at the beginning of the lower part of the conduit;
[m] – dynamic head in the operating mode;
[m] – total length of the penstock;
[m/s] – maximum water flow velocity in the pipeline at head in the operating mode;
[s] – shortest total closing time of the conveyance system (distributor) from 100 to 0;
[s] – shortest total opening time of the conveyance system (distributor) from 0 to 100;
[s] – characteristic time of the conduit (startup time, i.e., time of conduit inertia);
[m/s] – velocity of pressure wave propagation

## Slide 18: 3.3. Penstocks 3.3.3. Hydraulic Ratios and Sizing Laws
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Cases of Sudden Changes in Operating Mode
Sudden Linear Changes in Operating Mode
If , then all possible linear changes in the operating mode (maneuvers) of the water conveyance system can be defined as 'sudden.'
In the most critical cases of opening and closing, with an appropriate increase or decrease in pressure, in percentage of the dynamic pressure [m] at the end of the lower part of the conduit can be determined using the expression (ALLIEVI):
is the maximum value of pressure increase or decrease at the beginning of the lower part of the conduit
The times and can be expressed as follows:
,
The largest values of pressure increase or decrease occur starting from the lower part of the conduit at distances:
, for pressure increase;
, for pressure decrease.

## Slide 19: 3.3. Penstocks 3.3.3. Hydraulic Ratios and Sizing Laws
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Cases of Sudden Changes in Operating Mode
Sudden Closure of Pelton Turbine Nozzles
If there is a sudden closure of nozzles on the penstock with Pelton turbines, a critical pressure increase occurs in all segments of the penstock in the amount of:
where is the coefficient from the Allievi expression, and the other symbols have the same meanings as in the previous equations.
Shutdown of Generating Units (Aggregates) from the Grid
For Pelton turbines, as well as for Francis turbines equipped with "parallel discharge" (flow control) regulators, there are no specific issues because in case of a unit outage, the water supply is immediately closed. In the case of Pelton turbines, this is done by deflecting the jet, and in the case of Francis turbines, the parallel discharge assumes the full flow.

## Slide 20: 3.3. Penstocks 3.3.3. Hydraulic Ratios and Sizing Laws
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Cases of Sudden Changes in Operating Mode
Francis Turbine without Parallel Discharge
In the event of a unit outage at full load from the electrical grid, the water conveyance system immediately undergoes a maneuver to completely close. In this case, there is a pressure increase [%] and an increase in the speed of the unit (group) [%], which can be accurately calculated using the following relationships:
under the condition that , and
The closure time of the conveyance system (distributor) of the turbine can be approximately determined using the expression:

## Slide 21: 3.3. Penstocks 3.3.4. Guidelines for Dimensioning and Estimation of Weight
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Forces and Stresses
The main forces acting on the penstocks are due to internal pressure, weight, and temperature.
The most unfavorable conditions should be considered comprehensively for each characteristic location in the system. The forces acting on the penstock can be classified into the following groups:
Forces that are constantly acting, and their action is caused by:
- the internal pressure, including pressure shocks during a maneuver;
- their own weight and the weight of the water mass;
- temperature changes;
- pressure from the ground.
(2) Transient forces, which occur as a result of:
- filling and emptying;
- underpressure during operational (drive) maneuvers (pumped hydro power plants);
- wind and snow loading.
(3) Special forces, which occur in cases such as:
- pressure tests in factories or after installation;
- failure of safety devices;
- earthquakes;
- landslides, snow avalanches, etc.

## Slide 22: 3.3. Penstocks 3.3.4. Guidelines for Dimensioning and Estimation of Weight
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Forces and Stresses
The mentioned forces lead to the following stresses:
Tangential stresses (hoop stresses);
Radial stresses;
Longitudinal stresses.
Tangential Stresses. To dimension pipes under the load of internal pressure for tangential stress, the following equations are used:
For pipes with large wall thicknesses, the calculation should be performed using the Lamé equation:
– tangential stress [Pa=N/m2];
– internal pressure [Pa=N/m2];
– outer and inner diameter [m];
– mean radius [m];
– wall thickness [m].

## Slide 23: 3.3. Penstocks 3.3.4. Guidelines for Dimensioning and Estimation of Weight
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Forces and Stresses
Radial Stresses. Depending on the loading conditions (external pressure, internal pressure, earth pressure, etc.), radial stress reaches its maximum value at the location of the load application and then rapidly decreases to zero through the wall thickness.
Longitudinal Stresses. The forces acting in the longitudinal direction and the resulting stresses consist of the self-weight of the pipe, cross-sectional contraction, friction in the bearings, and expansion joints, hydrostatic pressure from dilation, forces at curvature locations, longitudinal stresses from bending, and thermal forces.
According to the three principal stresses, dimensioning can be carried out using the 'equivalent' stress based on the hypothesis of a state change. This stress is given by the expression:
For penstocks where , it is obtained:

## Slide 24: 3.3. Penstocks 3.3.4. Guidelines for Dimensioning and Estimation of Weight
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Allowable Stresses and Safety Factors
The allowable stress is usually expressed as a fraction of the stress corresponding to the yield strength, or the stress corresponding to the limits of damage, i.e.,
where or represents safety factors.
The term 'allowable stress' refers to the 'equivalent' stress
Different safety factors are distinguished:
Basic safety factor, ;
Material quality safety factor, ;
Manufacturing quality safety factor, ;
Calculation safety factor, ;
Environmental hazard and other factors safety factor,
The total safety factor, , is given by:

## Slide 25: 3.3. Penstocks 3.3.4. Guidelines for Dimensioning and Estimation of Weight
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Static calculations
Expressions for all types of stresses are given for smooth pipes
For concrete-coated steel pipes, the conditions are somewhat different. There are three structural elements involved: steel sheets, concrete layer, and coatings, so the conditions are similar to pipes with three layers. Here, the influence of concrete and coatings is crucial, as their participation in force transmission relieves the steel sheet of the penstocks.
In calculations, a concrete-coated pipe can be approximated in relation to a freely placed pipe by taking the factor , resulting in:
However, it should be emphasized that there is a rule for dimensioning concrete-coated pipelines.
While the full load from internal pressure can be carried by the steel pipe alone, without the involvement of concrete and coatings, the allowable tangential stress can reach up to 80-90% of the yield strength in the steel (in some cases, even up to 100% in extreme cases).

## Slide 26: 3.3. Penstocks 3.3.4. Guidelines for Dimensioning and Estimation of Weight
Components of a hydroelectric power plant and Methods of hydraulic and structural calculation of elements in modern hydroenergy facilities
Estimating the Mass
When determining the key parameters of hydropower plants or assessing the mass of individual components of the equipment, it is often necessary in practice to determine the order of magnitudes of the costs for the equipment with a tolerance of ±(5÷10)%. These estimates are necessary in the initial phases of hydroelectric project development, for example, when determining the construction sizes of the hydroelectric power plant. In this case, it's necessary to calculate the investment costs as a function of the installed flow rate, i.e.,
To achieve this, statistical data on mass obtained from a series of specific cases are also utilized.