## Slide 1: Modern Hydro Power Plants
Prof. Dr.sc. Gordana Janevska

## Slide 2: Operating Parameters of Hydropower Plants
Characteristic Curves and Parameters
Size of Hydro Power Plant Construction
  Selection and Presentation of Criteria
Number and Size of Units
Electricity consumption and production
  Consumption Factors
  Production Factors
Efficient design
  Modelling techniques
  Advanced materials
Digitalization in hydropower
  Asset performance management
  Condition monitoring equipment
  Outage management
  SCADA hydropower
  Internet of Things (IoT) in hydropower
  Artificial intelligence and machine learning

## Slide 3: 4.1. Characteristic Curves and Parameters
Operating Parameters of Hydropower Plants
The analysis of the hydrological conditions of the watercourse (performed by the hydrologist) results in the presentation of curves representing the available (potential) water quantities, which are provided in the form of average daily, weekly, monthly, and annual curves. These curves can be displayed in chronological order, i.e., water quantities arranged in chronological sequence, or as duration curves of flow, where flows are arranged by magnitude regardless of the time period in which they occur.
Curves of flow duration provide the fundamental data for the dimensioning of the hydroelectric facility. Using these curves, along with the curves of head duration, it is possible to obtain the curve for the duration of power at the generator terminals. These curves depict Q (flow), H (head), and P (power) as functions of time, with the values plotted in ascending order of magnitude, rather than in chronological order.

## Slide 4: 4.1. Characteristic Curves and Parameters
Operating Parameters of Hydropower Plants
Duration Curves of Flow, Heads, and Powers; Н-Р Curve for Run-of-River HPP

## Slide 5: 4.1. Characteristic Curves and Parameters
Operating Parameters of Hydropower Plants
Determining the actual or real production of the power plant is also important for other analyses, such as:
Incorporating the power plant into the energy system (power system),
Calculating profitability, and so on.
To determine the production of the power plant in three important periods – wet, dry, and average years – it is necessary to construct power curves as a function of flow through the hydraulic machines, i.e., the Р → Q curve or P = f(Q) curve.
To obtain the Р → Q curve, it is first necessary to calculate the efficiency levels.
The efficiency characteristic curves:
ηp – intake,
ηt – turbine,
ηg – generator,
ηtr – transformer,
ηv – high-voltage transmission lines
provide the overall efficiency of the power plant, ηтот, with the help of which the P = f(Q) curve can be constructed.

## Slide 6: 4.1. Characteristic Curves and Parameters
Operating Parameters of Hydropower Plants
Efficiency Curves of HPP with Three Production Groups
With the help of these curves, the curve can be constructed for any of the relevant gross heads (Hbr, maximum, average, or minimum) by entering the calculated values into the table or the diagram.
P = f(Q) Curve for HPP with Three Production Groups (Units)

## Slide 7: 4.1. Characteristic Curves and Parameters
Operating Parameters of Hydropower Plants
Tabular Representation of Values for Efficiency, Head, and Power of the HPP