## Slide 1: Modern Hydro Power Plants
Prof. Dr.sc. Gordana Janevska

## Slide 2: Operating Parameters of Hydropower Plants
Characteristic Curves and Parameters
Size of Hydro Power Plant Construction
  Selection and Presentation of Criteria
Number and Size of Units
Electricity consumption and production
  Consumption Factors
  Production Factors
Efficient design
  Modelling techniques
  Advanced materials
Digitalization in hydropower
  Asset performance management
  Condition monitoring equipment
  Outage management
  SCADA hydropower
  Internet of Things (IoT) in hydropower
  Artificial intelligence and machine learning

## Slide 3: 4.2. Size of Hydroelectric Power Plant Construction
Operating Parameters of Hydropower Plants
The size of hydropower plant construction refers to the maximum capacity of all installed facilities without reserves or the highest water consumption for all facilities [m3/s]. Properly selecting the size of construction is of utmost importance due to its impact on the rational and economic utilization of water power.
It is known that with the size of construction, the annual energy production increases according to a certain law, but at the same time, investment costs also increase. Since these two factors have opposing effects on the size of construction, a compromise solution should be found that will be economically most favorable under given conditions.

## Slide 4: 4.2. Size of Hydroelectric Power Plant Construction 4.2.1. Selection and Presentation of Criteria
Operating Parameters of Hydropower Plants
From several existing criteria, which may be more or less familiar, the following should be chosen:
1. Minimum production cost of energy;
2. Minimum operating costs for hydro power plant and additional thermal power plant;
3. Maximum increase in production value achievable through the sale of energy.
There are indeed various methods for selecting the economic sizes of construction for hydropower plants, but these methods go beyond the scope of this course.

## Slide 5: 4.2. Size of Hydroelectric Power Plant Construction 4.2.1. Selection and Presentation of Criteria
Operating Parameters of Hydropower Plants
1. Minimum production cost of energy
Investment costs and annual operational costs for the power plant depend on the installed capacity, i.e., the maximum water consumption.
Therefore, it is necessary to determine the investment costs, annual costs, and production for various sizes of construction in different areas where the minimum production cost is expected.
The investment quotient is
𝐵𝐻 – investments
Wk – useful production
The useful energy 𝑊𝑘 is obtained by assuming that around 90% of the physical production 𝑊𝐻 can be utilized
In order to obtain the values for , it is necessary to determine the costs for construction and energy, i.e., for useful production
The investment quotient is a function of the size of construction 𝑄1 [m3/s], i.e., 𝐶 = 𝑓(𝑄1), so that for certain values of 𝑄1, will obviously be minimal. This means that with a certain size of construction, the production cost will be minimal.

## Slide 6: 4.2. Size of Hydroelectric Power Plant Construction 4.2.1. Selection and Presentation of Criteria
Operating Parameters of Hydropower Plants
2. Minimum operating costs for hydro power plant and additional thermal power plant
To fully meet the demands of consumers, it is necessary to build not only a new hydroelectric plant but also an additional thermal power plant.
The economically optimal solution will be achieved when the total annual costs are minimized:
𝐴𝐻 – annual costs for the new hydroelectric plant
𝐴𝑇 – annual costs for the thermal power plant
and – constant annual costs
and – variable costs of the power plants, i.e., the increase in annual costs per unit capacity
and – installed capacity of the power plants
– production of the thermal power plant
– specific operational costs (fuel and lubrication)

## Slide 7: 4.2. Size of Hydroelectric Power Plant Construction 4.2.1. Selection and Presentation of Criteria
Operating Parameters of Hydropower Plants
2. Minimum operating costs for hydro power plant and additional thermal power plant
The condition for minimum costs
min capacity of the hydro power plant
, 𝑝𝑇 - annual production cost as a percentage (%) of the invested capital
∆𝐵𝐻, ∆𝐵Т - increase in investment costs depending on the installed capacity
If the relationship is graphically represented, two curves are obtained. First, there is the curve of as a function of the size of construction, which determines this derivative for different intervals of Qi . This curve decreases as Qi increases, and it represents the left side of equation. The other curve is obtained by graphing the right side of equation for different sizes of construction. The optimal size of construction lies at the intersection of these two curves.

## Slide 8: 4.2. Size of Hydroelectric Power Plant Construction 4.2.1. Selection and Presentation of Criteria
Operating Parameters of Hydropower Plants
2. Minimum operating costs for hydro power plant and additional thermal power plant
- required capacity of the network
The investment costs for the thermal power plant :
constant annual costs
If the future user area where a new hydroelectric plant needs to be built is specified, it can be covered by existing power plants and the new hydroelectric plant. If the user who can be covered by existing energy sources is excluded, the remaining user must be covered by the new hydroelectric plant. Since this hydroelectric plant will not be able to fully meet the network's needs due to the nature of available water quantities, thermal supplementation will be necessary. This thermal support can be provided by an additional thermal power plant or multiple thermal power plants that can be consolidated into one. If W represents the total annual energy demand, then covers the hydroelectric plant, and covers the thermal power plant.

## Slide 9: 4.2. Size of Hydroelectric Power Plant Construction 4.2.1. Selection and Presentation of Criteria
Operating Parameters of Hydropower Plants
2. Minimum operating costs for hydro power plant and additional thermal power plant
The annual energy costs for the hydroelectric plant
The annual energy costs for the additional thermal energy
- specific consumption of thermal energy
The total annual costs for the production of the required energy in the system
The cost of mixed energy per kWh
This calculation should be performed for several sizes of construction, each time considering the same user whose needs must be covered by the new hydroelectric plant and additional thermal power plant. For certain sizes of construction Qi , this cost will be minimal. This represents the optimal size of construction, Qi opt .

## Slide 10: 4.2. Size of Hydroelectric Power Plant Construction 4.2.1. Selection and Presentation of Criteria
Operating Parameters of Hydropower Plants
3. Maximum increase in production value achievable through the sale of energy
Hydropower plant should be built to a size where the production price can still be as high as, considering transmission losses, those can be achieved in the market. This criterion is particularly suitable in the case of energy export when sales prices are known or specified.
For various sizes of construction, it is needed to determine the increase in investment and the increase in production , and with a certain annual cost ratio , the increase in cost per kWh can be determine from the following expression:

## Slide 11: 4.2. Size of Hydroelectric Power Plant Construction 4.2.1. Selection and Presentation of Criteria
Operating Parameters of Hydropower Plants
Criteria:
1. Minimum production cost of energy;
2. Minimum operating costs for hydro power plant and additional thermal power plant;
3. Maximum increase in production value achievable through the sale of energy.
Analysis of hydro power plant construction sizes
BH – HPP investment; WH – available energy of HPP; C – investment quotient; Qi – installed flow of HPP; Z – variable cost of TPP (including fuel and oil); m=PH /PHi ; CM – price of mixed energy;
ΔC = ΔBk / ΔW – increase in energy price

## Slide 12: 4.2. Size of Hydroelectric Power Plant Construction 4.2.1. Selection and Presentation of Criteria
Operating Parameters of Hydropower Plants
For the economic analysis of pumped-storage hydropower plants, the following criteria can be applied (E.Indri, ENEL, Roma*):
1.
2.
3.
[$/kW] – annual unit cost of the installed capacity of the pumped hydropower plant (annual unit cost of the PHE capacity)
[$/kW] –the annual unit cost of the fuel-fired reference installation
𝑅 [$] – the total annual running cost of the hydro-electric station
𝐸 [kWh] – the average energy that can be produced per year, nrt of any energy that may be required for pumping water
𝑘 [$/kWh] – the cost of the fuel consumed in order to generate one kWh
𝑃𝑠 [kW] – firm capacity
𝑉 ($) – the limiting value of annual production of hydro-electric generating station