## Slide 1: Modern Hydro Power Plants
Prof. Dr.sc. Gordana Janevska

## Slide 2: Operating Parameters of Hydropower Plants
Characteristic Curves and Parameters
Size of Hydro Power Plant Construction
  Selection and Presentation of Criteria
Number and Size of Units
Electricity consumption and production
  Consumption Factors
  Production Factors
Efficient design
  Modelling techniques
  Advanced materials
Digitalization in hydropower
  Asset performance management
  Condition monitoring equipment
  Outage management
  SCADA hydropower
  Internet of Things (IoT) in hydropower
  Artificial intelligence and machine learning

## Slide 3: 4.3. Number and Size of Units
Operating Parameters of Hydropower Plants
Several factors influence the choice of the number and size of units (production groups), which in a certain sense determine the choice of the number and size of the aggregates. These factors include:
a) The maximum capacity from the perspective of technological capabilities for manufacturing;
b) Hydraulic utilization ratios and the role of power plants in the system;
c) Conditions of the electricity network with included production groups;
d) The required reserve capacity in the system;
e) Transportation conditions;
f) The standardization of production groups.

## Slide 4: 4.3. Number and Size of Units
Operating Parameters of Hydropower Plants
The maximum capacity is one of the crucial factors. So, for example, in the eighties of the last century, great progress was made in the construction of large aggregates, and what previously seemed like "maximum capacity", today is far exceeded. The fact is that conventional Francis turbines with capacities of 700 MW have been built, as well as reversible pump-turbines with capacities of 400 MW. In projects and studies, units of 1000 MW or more are also considered. Therefore, it can be concluded that the boundary of capacity is constantly changing, and it's difficult to determine where that boundary lies. This also applies to hydro-generators
Progress in the construction of a pump turbine and motor-generator

## Slide 5: 4.3. Number and Size of Units
Operating Parameters of Hydropower Plants
In terms of hydraulic relationships and the role of power plants, when choosing the number of units, the impact of the number of units on surplus or deficit production should be taken into account in terms of a larger or smaller number of units, as well as the efficiency of the power plant. Larger units have a higher level of efficiency, resulting in higher production. However, if the duration curve of the working water is such that the plant needs to operate at low flows, small units, or with a larger number of units for a given installed flow, are better suited to this mode.
Efficiency levels of a power plant with 2 and 3 units
relationships in the choice of 2 or 3 units

## Slide 6: 4.3. Number and Size of Units
Operating Parameters of Hydropower Plants
Investment costs increase with the increasing number of units.
If an increase in production is achieved with a larger number of units, and if the value of that production is equal to or greater than the increased annual operating costs corresponding to larger investments, it is justified to choose a larger number of units. It is assumed that a larger number of units provides higher production, which does not always happen.
Annual savings
ΔJ - savings on construction and equipment costs
k - annual cost rate (%)
Value of increased (decreased) production
ΔW - increase or decrease in annual production (kWh/year)
- price per kWh
If it s
it is justified to choose a smaller number of units if this relationship is satisfied.

## Slide 7: 4.3. Number and Size of Units
Operating Parameters of Hydropower Plants
The installed capacity in Power (𝑃𝑖) or flow rate (𝑄𝑖) can be divided into 2, 3, or more units. From an investment cost perspective, it is clear that efforts should be made to aim for a smaller number of units. This can be influenced by network requirements for limiting the capacity of a single unit, especially in smaller networks that, for example, in the case of reversible pump units, may not be able to withstand the starting impacts of the pump drive.
On the other hand, in hydroelectric facilities in small networks with a smaller number of power plants or production groups, the need for reserve capacity is treated differently than in larger systems, where a drop of, for example, 200 MW is not a problem.
The size of the unit in the construction of a series of power plants on a single watercourse can also be influenced by the tendency towards standardization of production groups. This means significant savings in projects, construction of the facility, and construction because part of the power plants can be built with the same production group.

## Slide 8: 4.3. Number and Size of Units
Operating Parameters of Hydropower Plants
Transportation requirements can sometimes be significant when choosing the size of the unit. If transport routes are limited due to size and transportation weights, this should certainly be taken into account. In the case of larger units, a solution is often found with multi-part spirals that are welded on-site, and generators are transported in multiple parts (three-part stators), and the rotor is also assembled in the field.