## Slide 1: Modern Hydro Power Plants
Prof. Dr.sc. Gordana Janevska

## Slide 2: Operating Parameters of Hydropower Plants
Characteristic Curves and Parameters
Size of Hydro Power Plant Construction
  Selection and Presentation of Criteria
Number and Size of Units
Electricity consumption and production
  Consumption Factors
  Production Factors
Efficient design
  Modelling techniques
  Advanced materials
Digitalization in hydropower
  Asset performance management
  Condition monitoring equipment
  Outage management
  SCADA hydropower
  Internet of Things (IoT) in hydropower
  Artificial intelligence and machine learning

## Slide 3: 4.4. Electricity consumption and production
Operating Parameters of Hydropower Plants
Electricity must be generated at the time it is needed because it cannot be stored and consumed whenever necessary. This is a significant difference between electrical energy and other forms of energy.
It is essential to understand the nature of electricity consumption in terms of time, intensity of demand, and other factors for the design and operation of power plants. This understanding allows power plants to efficiently produce the required amount of electrical energy. Among the fundamental concepts in this regard are consumption factors and production factors.

## Slide 4: 4.4. Electricity consumption and production 4.4.1. Consumption Factors
Operating Parameters of Hydropower Plants
When observing the consumer area connected to the network, which includes various electricity consumers such as households, administrations, industries, etc., with various electrical appliances and devices (ovens, heaters, motors, etc.), it becomes evident that each consumer uses energy differently. Their energy consumption throughout the day varies, and they utilize electrical energy either during specific times of the day or throughout the entire day. Each consumer demands power P, thereby loading the network or power plant with that power demand, and the curve P =f(t) is called the load curve or demand curve.
The highest load, or demand, from consumers is usually slightly less than their connected power capacity, P, because not all appliances of a specific consumer are connected simultaneously. If load curves from consumers of the same character are summed, a load curve of a set of consumers is obtained.
If the load curves of all existing groups of a certain user area are added together, a demand curve or a network load curve is obtained.

## Slide 5: 4.4. Electricity consumption and production 4.4.1. Consumption Factors
Operating Parameters of Hydropower Plants
Definition of consumption factors:
1. Connected load, P [kW] – of a system or a part of the system is equal to the sum of the nominal power ratings of all consumers connected to the system or part of the system.
2. Demand, 𝑃𝑝0 [kW] – for certain installations or systems is the instantaneous power or load that places a load on the energy source in a given time period.
3. Maximum demand or peak load, 𝑃𝑚 [kW] – of certain installations or systems is the highest load that will occur during the day.
4. Demand factor – of a system or part of the system is the coefficient of the maximum demand of the system or part of the system and the total connected load, i.e.
This factor is also known as the factor of simultaneity. It is always less than 1 or 100%.

## Slide 6: 4.4. Electricity consumption and production 4.4.1. Consumption Factors
Operating Parameters of Hydropower Plants
Definition of consumption factors:
5. Load factor – is the coefficient of the average power (P𝑠𝑟) and the maximum load or peak load (Pm). In each case, a period for which the average power (load) and the maximum demand are related must be defined mathematically, as follows:
It is always less than 1 or 100%
Annual Consumption Curve

## Slide 7: 4.4. Electricity consumption and production 4.4.1. Consumption Factors
Operating Parameters of Hydropower Plants
Definition of consumption factors:
6. Diversity factor – of a system or part of the system is the coefficient of the sum of peak loads of parts of the system or part of the system and the peak load of the entire system or part of the system, i.e.
, , … – peak loads of parts of the system. They are always greater than 1 or 100%.

## Slide 8: 4.4. Electricity consumption and production 4.4.1. Consumption Factors
Operating Parameters of Hydropower Plants
Load demand curves during a day are called daily curves, and there are also weekly, monthly, and annual demand curves.
The curve of daily load demand changes every day. If these curves from all the days of the year are combined into one curve, we get the curve of annual load demand. For simplicity, the average daily loads are taken, and they are plotted chronologically.
The curve of annual demand (consumption) (consumers, group of consumers, or network) has a shape similar to a sinusoid because the summer load is less than the winter load.
Average load:
W - annual energy consumption
number of hours in a year
𝑃𝑚 - maximum load in a year
𝑇𝑚 - the duration of the maximum load

## Slide 9: 4.4. Electricity consumption and production 4.4.1. Consumption Factors
Operating Parameters of Hydropower Plants
In practice, the so-called load duration curve, or demand curve, is often used. This curve is obtained by arranging the variable loads by magnitude, regardless of time. If daily or annual loads are sorted in this way, a duration curve for daily load or a duration curve for annual load is obtained.
Load Duration Curve (Demand Curve)
From the load duration curve, the duration of each load level during a day or throughout the year can be determined. The area under the load duration curve represents the daily or annual electricity consumption in kWh. This means that the area under the daily load duration curve gives the daily electricity consumption in kWh. The same principle applies to the annual load duration curve for annual electricity consumption.

## Slide 10: 4.4. Electricity consumption and production 4.4.2. Production Factors
Operating Parameters of Hydropower Plants
Due to losses in the network, both capacity losses (kW) and energy losses (kWh), the power plant must supply the network with greater capacity and energy than what corresponds to the network's consumption. Capacity losses in the transmission lines are approximately proportional to voltage drop, and energy losses are calculated based on network data. Energy losses amount to 10 – 30 % of the network's annual consumption, and capacity losses are around 10 – 15 %.
Accordingly, the power plant's maximum annual load, 𝑁𝑚, will be equal to the network's maximum load, 𝑃𝑚𝑚, plus the capacity losses in the network and the power consumed by the power plant itself. Because the power plant must have a certain reserve capacity for possible defects or extraordinary loads, power plants are built with a greater capacity than what was previously mentioned. This capacity is referred to as the installed capacity of the power plant, 𝑁𝑖.

## Slide 11: 4.4. Electricity consumption and production 4.4.2. Production Factors
Operating Parameters of Hydropower Plants
– installed capacity of the power plant
– maximum possible load on the power plant
– power plant's own consumption
– maximum demand or peak load on the network
– capacity losses in the network system (transmission lines and transformers)

## Slide 12: 4.4. Electricity consumption and production 4.4.2. Production Factors
Operating Parameters of Hydropower Plants
Definition of Production Factors
1. Plant Utilization Factor – The plant utilization factor of a power plant is the ratio of the maximum load on the generator (𝑁𝑚) to its nominal capacity (𝑁𝑖), i.e.
𝑁𝑠𝑟 - average load on the power plant
𝑁𝑒 - maximum possible load of the power plant
W - annual production of the power plant

## Slide 13: 4.4. Electricity consumption and production 4.4.2. Production Factors
Operating Parameters of Hydropower Plants
Definition of Production Factors
2. Plant Load Factor (PLF) – This factor is the ratio of the average load (𝑁𝑠𝑟) to the maximum load of the power plant (𝑁𝑚), i.e.
It is also the ratio between actual and potential production. It is always less than 1.
3. Plant Reserve Factor – This factor is the coefficient of installed capacity (𝑁𝑖) and maximum load (𝑁𝑚)
The time it would take to achieve the same actual annual production (W) if the power plant were operated at maximum load (𝑁𝑚) is called the duration (or utilization) of the maximum annual load 𝑇𝑚, which is given by the equation:

## Slide 14: 4.4. Electricity consumption and production 4.4.2. Production Factors
Operating Parameters of Hydropower Plants
The time it takes to achieve the same actual annual production as when the power plant operates at its installed capacity (𝑁𝑖) is called the utilization time of the installed capacity 𝑇𝑖 = 𝑊/𝑁𝑖 [h/year].
The annual production can be expressed as:
Duration Curve of Annual Load on Power Plant
The duration curve of annual load on power plant is of particular importance. The area under it gives the actual annual production of the power plant, and it can be used to determine the duration of individual loads, even when the load curves of daily loads are not known.
Moreover, the load duration curves can be approximated and mathematically expressed if only the maximum and minimum loads of the power plant are known, as well as the duration of the maximum annual load 𝑇𝑚. Using load duration curves, one can further determine the allocation of loads among two or more power plants, as well as the annual losses in the power lines and structures.