## Slide 1: Modern Hydro Power Plants
Prof. Dr.sc. Gordana Janevska

## Slide 2: Operating Parameters of Hydropower Plants
Characteristic Curves and Parameters
Size of Hydro Power Plant Construction
  Selection and Presentation of Criteria
Number and Size of Units
Electricity consumption and production
  Consumption Factors
  Production Factors
Efficient design
  Modelling techniques
  Advanced materials
Digitalization in hydropower
  Asset performance management
  Condition monitoring equipment
  Outage management
  SCADA hydropower
  Internet of Things (IoT) in hydropower
  Artificial intelligence and machine learning

## Slide 3: 4.5. Efficient design
Operating Parameters of Hydropower Plants
The potential for electricity production in a hydropower plant depends upon the hydrology, topography and design of the power plant. Several parameters help determine the efficiency of the power plant:
the amount of water available;
water loss due to a flood spill, bypass requirements or leakage;
the difference in head between upstream intake and downstream outlet;
hydraulic losses in water transport due to friction and velocity changes;
the efficiency in energy conversion of electromechanical equipment.

## Slide 4: 4.5. Efficient design
Operating Parameters of Hydropower Plants
The energy transformation process in modern hydropower plants is highly efficient and usually well over 90% for mechanical efficiency in turbines and over 99% in the generator. The loss of efficiency is due to:
hydraulic losses in the water circuit (intake, tunnel, penstock, turbine and tailrace);
mechanical losses in the turbo-generator group;
electrical losses in the generator, transformer and power ducts.
In addition, the efficiency of plants depends to a great extent upon the reliability and availability of the equipment, which can be affected by aging, wear and tear, sudden outages, etc.

## Slide 5: 4.5. Efficient design 4.5.1. Modelling techniques
Operating Parameters of Hydropower Plants
The efficiency of electromechanical equipment, especially turbines, can be improved by better design and by also selecting a turbine type with an efficiency profile that is best suited to the duration curve of the inflow. It is therefore important to accurately model turbulent flow and system performance for a wide range of discharge rates. Computer tools are used to find designs that avoid vortices and related pressure pulsations and cavitation caused by the movement of water through the turbine. They are also used for optimising the interaction of the electromagnetic field of the generator’s rotor with the stator and to predict the build-up of heat in generators and subsequently the flow of cooling air or water needed to keep temperatures down.

## Slide 6: 4.5. Efficient design 4.5.1. Modelling techniques
Operating Parameters of Hydropower Plants
The main design tools used by the hydropower industry are laboratory reduced-scale physical models and computational models. Hydraulic models (both laboratory and numerical) are generally used to simulate conditions for environmental enhancement, dam operation and turbine design and optimization.
The sharp increase in computational power in recent years has led to significant use in the hydropower industry of computational fluid dynamics (CFD) models, which use numerical methods to represent the physics of fluid in motion in the complex water systems of a hydropower facility.

## Slide 7: 4.5. Efficient design 4.5.2. Advanced materials
Operating Parameters of Hydropower Plants
The flexible use of hydropower can cause some problems for electromechanical equipment as many hydro plants have not been designed to provide balancing power continuously. The biggest challenges are:
frequent start and stops (20 or more per day for pumped hydro in contrast to 3 per day formerly), and the mechanical and temperature-related stress that they put on the stator winding insulation;
fast response, meaning adjustment of operating point several times per minute and the associated wear and load on the regulating mechanisms;
voltage peaks due to the frequency converter, and their effect on the generator winding insulation.

## Slide 8: 4.5. Efficient design 4.5.2. Advanced materials
Operating Parameters of Hydropower Plants
The cavitation, draft tube pressure pulsations and vibrations are also more likely under these operating conditions with frequent start and stops, thus damaging electromechanical equipment. Moreover, high concentrations of hard particles in the water, especially hard and angular ones such as quartz and feldspar, can harm certain turbine parts, quickly abrading surfaces and causing the turbines to become less efficient. Surfaces exposed to a high relative water velocity are damaged the most. For Francis turbines, the eroded parts are mainly the guide vanes, facing plates, labyrinths and runners; for Pelton turbines, they are the runners and injectors. These parts may need to be treated almost as a consumable and overhauled or even replaced after each flood season.

## Slide 9: 4.5. Efficient design 4.5.2. Advanced materials
Operating Parameters of Hydropower Plants
In reservoirs, sediments may have time to settle, but in run-of-the-river projects most of the sediments may follow the water flow to the turbines. The traditional solution to the problem has been to build de-silting chambers to trap the silt and then to flush it out into bypass outlets, but it is very difficult to trap all particles, and especially the fine ones. New solutions are being developed by coating steel surfaces with a very hard ceramic coating, protecting against erosive wear or at least delaying the process.
There are high direct costs associated with repairing and replacing cavitation damaged turbine blades. However, materials science applications such as Cold Spray, may reduce the cost of deploying new hydropower or extend the lifespan of existing hydropower projects. Similar to cold spray, friction stir processing creates novel compounds that can be stronger and longer lasting than the base metal, giving components new life or making new components cheaper by only requiring high performance materials at stress and wear points.

## Slide 10: 4.5. Efficient design 4.5.2. Advanced materials
Operating Parameters of Hydropower Plants
A more effective solution is to use protective coatings. These increase the time between overhaul by a factor of between two and five and reduce the damage to some specific turbine parts by an even greater amount. Longer periods of operation imply higher generation, helping investments to be paid off more quickly by minimizing damage from hydro-abrasive erosion. Therefore, precautions against hydro-abrasive erosion should ideally be taken at the time the plant is designed. Improvements in material development have been developed for almost every plant component.